Annexure –B to ARR & ERC MYT petition for 2018-19 to 2021-22

Capital Expenditure Plan for MYT Control Period 2018-19 to 2021-22

CSEZA Intends to undertake the capital works detailed below during the MYT control period  2018-19 to 2021-22.

| S.No | Year | Estimated Amount-Rs lakh | Financing Plan |
| --- | --- | --- | --- |
| 1 | 2018-19 | 24.97 | From Surplus in CSEZA’s Power Distribution System Account |
| 2 | 2019-20 | 284.20 |  |
| 3 | 2020-21 | 14.69 |  |
| 4 | 2021-22 | 14.15 |  |

The abstract and details of capital works planned with necessity, reasons/justification as well as cost estimate are furnished below.

| 2018-19 |  |  |  |
| --- | --- | --- | --- |
| Sl.No | Name of Work | Estimate Amount (Lakhs) | Expected Date of Completion |
| 1 | Purchasing of 15 Nos 3G /4G modem for the Web enabled Pre-paid Metering System. | 2.27 | 10.06.2018 |
| 2 | Construction of Fencing around 110 KV Sub-Station | 3.30 | 12.09.2018 |
| 3 | Construction of Aluminium fabrication works for operator cabin room at 110 KV Substation control room | 1.25 | 25.10.2018 |
| 4 | Supply Installation testing and commissioning of 2 Nos Air Conditioners at 110 KV Substation | 0.78 | 25.10.2018 |
| 5 | Purchasing of 3 Nos Earth rod for the use of 110 KV substation | 0.15 | 01.01.2019 |
| 6 | Purchasing of 5 kVA inverter with Battery for 110 KV Substation | 1.25 | 01.02.2019 |
| 7 | Purchasing of 10 Nos Energy Meter for Power Distribution System | 2.44 | 01.02.2019 |
| 8 | Construction of Store Room in 110 KV Substation | 9.60 | 15.03.2019 |
| 9 | Purchasing of 25 Nos 3G /4G modem for the Web enabled Pre-paid Metering System | 3.93 | 01.03.2019 |
|  | Grand Total | 24.97 |  |

| 2019-20 |  |  |  |
| --- | --- | --- | --- |
| Sl.No | Name of Work | Estimate Amount (Lakhs) | Expected Date of Completion |
| 1 | Purchase of 1 No. Megger Unit | 0.30 | 15.04.2019 |
| 2 | Purchase of Computer Peripherals & Office Equipment’s | 2.65 | 30.04.2019 |
| 3 | Replacement of Existing Isolator type HT Panel in SDF 16 (one incoming & 6 no’s outgoing feeders) with IP 67 Indoor VCB Type HT Panel | 27.00 | 30.05.2019 |
| 4 | Replacing of 30 V, 40 Ah battery bank for 1250 KVA transformer No.2 at SDF-17 | 0.45 | 12.06.2019 |
| 5 | Supply installation Testing & Commissioning of new 400 kWp Grid Tied Solar Plant | 236.00 | 30.09.2019 |
| 6 | Supply, Installation, testing and Commissioning of 2 Nos 110kV, 31.5kA, 800A triple pole, centre post rotating, horizontal double break isolator without earth switch in 110 KV Substation Yard in Metering side. | 9.30 | 14.08.2019 |
| 7 | Supply, Installation, testing and Commissioning of RTU in 110 KV Substation for obtaining open access consent. | 4.50 | 31.08.2019 |
| 8 | Purchasing of 25 Nos 3G /4G modem for the Web enabled Pre-paid Metering System | 4.00 | 15.12.2019 |
|  | Grand Total | 284.20 |  |

| 2020-21 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sl.No | Name of Work |  | Estimate Amount (Lakhs) |  | Expected Date of Completion |  |
| 1 | Purchasing of 10 Nos Energy Meter for Power Distribution System |  | 2.44 |  | 01.05.2021 |  |
| 2 | Purchasing of 1 No. 11/ 0.415 KV 500 KVA trolley mounted type Unitised Transformer as spare in Power distribution system. |  | 8.00 |  | 16.07.2020 |  |
| 3 | Purchasing of 25 Nos 3G /4G modem for the Web enabled Pre-paid Metering System |  | 4.25 |  | 15.12.2020 |  |
|  | Grand Total |  | 14.69 |  |  |  |
| 2021-22 |  |  |  |  |  |
| Sl.No | Name of Work | Estimate Amount (Lakhs) |  | Expected Date of Completion |  |
| 1 | Replacing of 30 V, 40 Ah battery bank for control system of 1250 KVA No1 transformer at SDF-17. | 0.45 |  | 10.04.2021 |  |
| 2 | Replacing of 30 V, 40 Ah battery bank for control system of 1250 KVA distribution Transformer at SDF-43 | 0.45 |  | 10.04.2021 |  |
| 3 | Purchasing of 10 Nos Energy Meter for Power Distribution System | 3.00 |  | 10.08.2021 |  |
| 4 | Purchasing of 25 Nos 3G /4G modem for the Web enabled Pre-paid Metering System | 4.25 |  | 10.10.2021 |  |
| 5 | Supply of 2 Nos 110 KV.800 A triple pole Isolators as spare in110 KV substation | 6.00 |  | 10.12.2021 |  |
|  | Grand Total | 14.15 |  |  |  |

Details of Capital Works planned for 2018-19

- Procurement of 3G/4G GPRS Modem for Web Enabled Pre-paid Energy Metering System

Need & Necessity

CSEZA has 156 Nos of pre-paid energy meters for their HT & LT Consumers. These real time data from energy meters are communicated using GPRS modems to the computer server installed for web enabled pre-paid metering System .The data communication speed of existing 2 G modem used for communicating data from energy meters provided is very low., in order to improve the data communication speed, it is proposed to replace the existing 2G modems with 3G/4G modems.in a phased manner. As first phase it is planned to replace 15 Mos of modems with an estimate amounting Rs. 2, 26,800/-

| Sl No. | Description of Items | Qty | Rate (Rs.) | Amount (Rs.) |
| --- | --- | --- | --- | --- |
| 1 | Supply of 3G GPRS Modem (Model No. F2414- Four Faith Make) for Web Enabled Energy Monitoring System | 15 Nos | 15,120.00 | 2,26,800. |

- Construction of fencing around 110 KV CSEZ Substation Control Room building.

Need & Necessity:

The 110 KV substation is the heart of CSEZA’s power distribution system. Presently fencing in this substation is provided only around the yard. It is highly necessary to make an additional fencing around substation control room premises also to ensure the safety and to restrict the unauthorized entry. The details and specification of fencing prposed is given in the estimate below. The total estimate cost works out to Rs: 3, 30,000.

| Estimate for Construction of Additional Fencing around 110 KV Substation Control Room building. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Item | Unit | Qty. | Unit Rate (In Rs.) | Total Amount |
| A1 | Earth work in excavation below ground level for all kinds of works in all types of soils except soft rock and hard rock as classified in specification for a depth upto 1.5 m including removal of vegetation, slopes, levelling, grading and ramming of bottoms, dewatering of accumulated water from any source and keeping the surface dry for subsequent works and disposal or stacking of excavated material within a lead of 100m, as directed including providing temporary supports to existing service lines like water pipes, sewage pipes, electric overhead and underground cables etc. complete all as per direction/approval of the Engineer In Charge. , but excluding shoring and strutting. | cum | 8 | 4200 | 33600.00 |
| A2 | Backfilling after execution of the work to proper grade and level with selected materials from available excavated soil from spoil heaps within a lead of 100m, including re-excavating the deposited soil excavated earlier, breaking clods, laying at all depths and heights in layers of thickness not exceeding 15cms, watering, rolling and ramming by manual methods/mechanical compactors to achieve 90% laboratory maximum dry density, dressing, trimming etc. in foundations, plinths, trenches, pits etc. complete all as per direction/approval of the Engineer In Charge. | cum | 4 | 4000 | 16000.00 |
| A3 | Providing and constructing Random rubble masonry using hard granite stones in cement mortar 1:6 including curing etc., complete as per specifications in foundation and plinth and complete all as per direction/approval of the Engineer In Charge. | cum | 6 | 4,200. | 25200.00 |
| A4 | Providing and laying plain cement concrete in foundations etc. including shuttering, tamping, ramming, vibrating, curing, etc. all as specified in any shape, position , thickness and finishing the top surface , rough or smooth as specified and directed all complete for all concrete of nominal mix 1:5:10 by mass (1 cement: 5 coarse sand: 10 crushed stone aggregate/gravels) with 40mm and down size graded crushed stone aggregates / gravels, all materials including cement supplied by the contractor etc. complete all as per direction/approval of the Engineer In Charge. | cum | 1 | 4,500. | 4500.00 |
| A5 | Providing and laying reinforced cement concrete of M-30 grade with 20mm and down size graded crushed stone aggregates/ gravel in super structure in columns , walls, slabs etc providing cement wash (wherever no other surface application is specified), providing pockets, openings recesses, chamfering etc. wherever required, vibrating, tamping, curing and rendering if required to give a smooth and even surface etc. (Excluding the cost of reinforcement, shuttering & specified admixtures) for all heights in any shape, position and thickness etc all complete as specified, shown and directed. All materials including cement supplied by the contractor. | cum | 10 | 4070. | 40700.00 |
| A6 | Providing and fixing centring and shuttering in superstructures in column, walls, slabs etc. for all depth below and up to and inclusive of plinth level including shuttering for single our concreting, strutting, bracing, propping etc. keeping the same in position during concreting and removal of the same after specified period etc. for straight/ inclined shuttering, keeping necessary provision for projecting dowels, anchor bolts or any other fixture etc. complete and as specified and directed | Sq.m | 66 | 700 | 46200.00 |
| A7 | Supplying and placing in position high yield strength deformed steel bars reinforcement of grade Fe 500 (D) conforming to IS : 1786 , for RCC work including transporting the steel , straightening , cleaning , decoiling, cutting, bending to required shapes and length as per details, binding with 18 SWG black soft annealed binding wire at every intersection, supplying and placing with proper cover blocks, supports, chairs, overlaps, welding, spacers, fan hooks etc. for all heights and depths etc. complete all as per direction/approval of the Engineer In Charge. Supply of material in the contractor's scope. | MT | 0.50 | 1,03,000. | 51500.00 |
| A8 | Plastering 15mm thick with cement mortar 1:4 (1 cement: 4 fine sand), , finished smooth including scaffolding, curing etc., complete for ALL SURFACES of random rubble /brick masonry works for all heights etc. complete all as per direction/approval of the Engineer In Charge. | sq.m | 250 | 34.80 | 8700.00 |
| A9 | Chain link fabric fencing mesh of size 50x50mm made of GI wire of dia 4mm s including the cost of materials, labour, scaffoldings /staging if required, finishing of the joints etc. complete all as per direction/approval of the Engineer In Charge. | sq.m | 150. | 300. | 45000.00 |
| A10 | Providing and fixing steel doors made out of standard MS medium class hollow tube sections. The shutters shall be of MS tubes for styles, rails and intermediate members and fixed with MS sheets (single / double skin) including providing and fixing approved pivots as required and hinges transom coupling member etc., including cleaning the surface thoroughly free from rust scales and painted with two coats of epoxy paint over a coat of red oxide zinc chromate primer conforming to IS specifications including providing and fixing MS aldrops, MS tower bolts and MS handles etc., complete all as per specifications and as per direction/approval of the Engineer In Charge.. | kg | 100. | 58. | 5800.00 |
| A11 | Supplying, fabricating, assembling, hoisting/erecting and fixing in position at all heights and with all leads, structural steel works of welded built-up sections, all as per site condition and according to the fencing that is going to be placed etc.., as per detailed specifications and as per direction/approval of the Engineer In Charge. |  |  |  |  |
|  | i) MS Angles, tees, flats, etc… | MT | 1. | 11,000 | 11000.00 |
|  | ii) With Factory made MS Holding down foundation bolts including nuts and washer plates of any dia including necessary threading and machining. | kg | 100. | 59. | 5900.00 |
| A12 | Painting wall plastered surfaces with two or more coats of super acrylic emulsion paint of approved brand and colour (Berger or Asian or equivalent) to give an even shade with required finish over a coat of water thinnable cement primer including cleaning the surfaces, filling the crevices with approved filler, scaffolding, curing, etc., complete all as per specifications at all heights and as per direction/approval of the Engineer In Charge. | Sq.m | 300. | 80. | 24000.00 |
| A13 | Providing and finishing two or more coats with EPOXY PAINT of approved make at all locations prepared & applied as per manufacturer's specifications including providing approved epoxy putty, preparation of surface, scaffolding etc., complete at all heights and as per direction/approval of the Engineer In Charge... | Sq.m | 70. | 170. | 11900.00 |
|  | TOTAL |  |  |  | 3,30,000. |  |  | 921570.00 |

- Construction of Aluminium fabrication works for operator cabin room at 110 KV Substation control room

Need and Necessity

Due to the emission of heat radiation from 11 KV feeder control panels in substation building the room temperature is way higher than usual, Also, there is complaint from substation operator that at times, there is foul smell entering inside substation from the nearby Chemical industries and from the Common effluent treatment plant.. Hence it has become difficult for the operating staff to work without an operator cabin room partitioning at substation control room. Therefore it is proposed to construct a cabin room in the existing 110KV CSEZ, Substation, Kakkanad for the use of operating staff at control room. The cost of Estimate is about Rs. 1, 25,000/-.

| Sl No | Name of work | Qty | Estimated cost |
| --- | --- | --- | --- |
| 1 | Construction of Aluminium fabrication works and constructing one operator cabin room partition at CSEZ 110 KV Substation control room using aluminium fabrication with glass. | one | Rs. 1,25,000/- |

- Supply Installation testing and commissioning of 2 Nos Air Conditioners at 110 KV Substation.

Need and Necessity

As stated in 3 above, an operator cabin has to be made inside substation Control Room and the same has to be air-conditioned. The cost of providing 2 Nos Air Conditioner unit in control room is estimated for Rs 78,415/-.

| Sl No | Name of Work | Qty | Estimated cost |
| --- | --- | --- | --- |
| 1 | Supply Installation testing and commissioning of 2 Nos Air Conditioners at 110 KV Substation CSEZ, Kakkanad | Ls | Rs. 78,415/- |

- Purchasing of 3 Nos Earth rod for the use of CSEZ substation

Need & Necessity

The earth rod is used in 110 KV substation for discharging the electrical equipment’s and cable conductors during outage of maintenance works in power distribution system to avoid electrical shocks from the induced current in the cable conductor. The present earth rod in use is damaged and new 3 Nos earth rods are necessary to carry out the preventive maintenance works and breakdown maintenance works safely. The estimate cost for procuring 3 Nos earth rods are Rs: 15,000/- only.

| Sl No | Name of work | Qty | Rate |  | Estimated cost |
| --- | --- | --- | --- | --- | --- |
| 1 | Supply of 3 NosEarth rods for using up to 110 KV at 110 KV Substation CSEZ, Kakkanad | 3 Nos | 5000 |  | Rs. 15,000/- |

- Purchasing of 5 kVA inverter with Battery for 110 KV Substation

Need & Necessity

The 110 KV substation have a 5 KVA inverter with Battery for the DC control supply to the auxiliary relays in control room. These Inverter systems are very old, installed many years back and performance is not satisfactory. The substation relays and its control supply are very critical hence, replacing of these inverter with battery system are urgent. The cost of estimate is Rs: 1, 25,000/.

| Sl No | Name of Work | Qty | Estimate Amount |
| --- | --- | --- | --- |
| 1 | Supply and installation of one 5 kVA inverter with Battery Set for 110 KV Substation Control room | 1 | 1,25,000 |

- Purchasing of Prepaid Energy Meter for Power Distribution System

Need & Necessity

CSEZA following presently prepaid metering systems, to ensure collection of electricity charges properly from consumers in advance. Now the entire CSEZA Consumers are connected using pre-paid energy meters and consumer’s readings are recorded electronically through web enabled system. This proposal for procure10 nos. pre-paid energy meters are essential in order to have adequate spare meters to cover meter failure and to ensure the new service connections are to be given in time. The total estimate cost is Rs 2, 43,540/-.

| Estimate for Purchasing of Prepaid energy Meter for Power Distribution System |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of Prepaid Energy Meter (Model No. Power logic ION 6200 Schneider Electric Make) for Power Distribution System | Nos | 10 | 24,354 | 2,43,540 |

- Construction of Store Room in 110 KV Substation

Need & Necessity

Presently 110 KV Substation Control Room includes a Storage place with roofing sheet supported by tubular structures at corners without all-round walls. The existing open storage area is insufficient to store all the spare items and electrical materials like CSS transformer, LBS switches, measuring equipment and tools etc. In order to have a closed and protected store room to keep spares and valuable items, it is proposed to construct store room. This enables to get more area for stacking materials and spares properly. Therefore the above proposal includes providing brickwork around the existing storage area including plastering and painting the same. For access, a steel door is also proposed and to be painted with epoxy paint so as to make it free from corrosion.

Thus, more materials like transformers and other electrical items are able to be stored over that particular area safely without causing any damages to the stored items. The Estimate cost is Rs: 9, 55,152/-.

| Estimate for Construction of Store Room in 110 KV Substation. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Item | Unit | Qty. | Unit Rate (In Rs.) | Total Amount |
| A1 | Providing and laying brick masonry with brick of class 5.0 in cement mortar 1:6 (1 cement: 6 Sand) in one or more brick thickness and in any shape at all heights including the cost of materials, labour, scaffoldings /staging, sampling and testing, soaking of bricks, cutting and laying of bricks, finishing of the joints, curing etc. complete all as per direction/approval of the Engineer In Charge. All materials including cement supplied by the contractor. | cum | 20. | 6,500. | 1,30,000. |
| A2 | Plastering 15mm thick with cement mortar 1:4 (1 cement: 4 fine sand), , finished smooth including scaffolding, curing etc., complete for ALL SURFACES of random rubble /brick masonry works for all heights etc. complete all as per direction/approval of the Engineer In Charge. | sqm | 220. | 270. | 59,400. |
| A3 | Providing and finishing two or more coats with EPOXY PAINT of approved make at all locations prepared & applied as per manufacturer's specifications including providing approved epoxy putty, preparation of surface, scaffolding etc., complete at all heights and as per direction/approval of the Engineer In Charge. | sqm | 45. | 400. | 18,000. |
| A4 | Aluminium fixed glazed doors with approved make sections, friction hinges, cast aluminium handle etc, all complete with approved shade electrostatically powder coated aluminium sections and 6mm thick toughened glass as per IS:5437. | sqm | 71. | 7,000. | 4,97,000. |
| A5 | Supplying & laying Vinyl flooring of 2mm thick at floor areas of Substation including cost of necessary surface preparation, cleaning, material, labour charge etc, all as per direction/approval of the Engineer In Charge | sqm | 300. | 600. | 1,80,000 |
|  | TOTAL |  |  |  | 8,84,400. |
|  | PMC Charge |  |  |  | 70,752 |
|  | Grand Total |  |  |  | 9,55,152 |

- Procurement of 3G/4G GPRS Modem for web Enabled Pre-paid Energy Metering System.

Need & Necessity

As stated in the  capital works under S.NO 1 above, it is proposed to procure additional  25 No’s of new 3G/4G GPRS modem  with an estimated amount of Rs. 3,93,000/-

| Estimate for purchasing of 3G GPRS Modem for web Enabled Pre-paid energy monitoring System |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of 3G GPRS Modem (Model No. F2414- Four Faith Make) for Web Enabled Energy Monitoring System | Nos | 25 | 15,720. | 3,93,000 |

Details of Capital Works planned for 2019-20

- Purchase of one Megger (Insulation testing equipment) for the use of 110 KV Substation and power distribution system.

Need & Necessity

The existing Megger (Insulation testing equipment ) available for the power distribution system at 110 KV substation is very old and recently it became faulty. The same was purchased more than 10 years back and is unserviceable now. Hence, it is required to procure a new megger unit for insulation testing of power circuits, transformers and other equipment in power distribution system. The estimate cost for procuring one megger unit is about Rs.30, 000/-.

- Procurement of Computer Peripherals & Office Equipment

Need & Necessity

CSEZA envisages for procuring certain additional computer peripherals like lap top, printers, scanners and office equipment’s etc. for the substation & administration office for exclusive use of Power distribution System works. The estimate cost for the same works out to Rs : 2,64,950/-

| Estimate for Procuring of Computer peripherals & Office Equipment’s |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl No. | Description of Items | Qty | Unit | Rate (Rs.) | Amount (Rs.) |
| 1 | Desktop Computer | 3 | Nos | 40000 | 1,20,000 |
| 2 | Lap top | 1 | Nos | 54000 | 54,000 |
| 3 | Windows 7 Professional Software | 3 | Nos | 9500 | 28,500 |
| 4 | Hard Disk for NAS | 2 | Nos | 12400 | 24,800 |
| 5 | ADSL Modem | 1 | Nos | 1800 | 1,800 |
| 6 | Lap top LCD Screen | 2 | Nos | 4800 | 9,600 |
| 7 | Key board & Mouse | 2 | Nos | 950 | 1,900 |
| 8 | Network Cable and connections | 1 | set | 2200 | 2,200 |
| 9 | Wi-Fi dongle for desktop | 3 | Nos | 850 | 2,550 |
| 10 | Printer Cartridge Colour | 8 | Nos | 850 | 6,800 |
| 11 | Printer Cartridge Black | 3 | Nos | 2600 | 7,800 |
| 12 | Service Charges | LS | LS | 5000 | 5,000 |
|  | Grand total |  |  |  | 2,64,950 |

- Replacement of Existing Isolator type HT Panel with New IP 67 Indoor VCB Type HT Panel in HT distribution System near SDF-16 building at CSEZ

Need & Necessity

The existing HT Panels make of ELECTROTECNICA, KOLKATA installed at SDF 16 in CSEZ power distribution system are about 17 years old (2001 model).This panel have 6 nos 11 KV 630 Amps load break switches without overload protection. Now it is very difficult to obtain its spare parts for repair and maintaining the same. The existing LBS type HT panel serving power supply to 3 Nos of HT consumers and 17 Nos LT power consumers in that area. Now frequent power failures occurred in SDF 16 due to flash from LBS in this HT panels and causing supply interruption to the consumers in 11 KV Ring 2B feeders.

In view of the above, in order to ensure the safety of work men and to avoid electrical fire hazard, it is required to replace the existing LBS type HT panels in SDF 16 with new HT panels having VCB protections are highly essential to operate the 11 KV UG feeders safely and to provide uninterrupted power supply to the HT& LT consumers in Ring 2B feeder.

CSEZA had proposed for the replacement of this old HT panel earlier in MYT petition 2015-18. In this regard and in principle approval was obtained from KSERC. Due to administrative reasons the above work was not implemented. In view of the above CSEZA again include this work on new MYT petition 2018-22 for completing the same during 2019-20.The total Estimate Cost is Rs: 27 Lakhs

| Estimate for Replacing Existing Isolator type HT Multi Panel with New IP 67 Indoor VCB Type HT Panel in HT distribution System near SDF-16 building |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SLNo | Item Description | Unit | Qty | Rate | Amount |
| 1 | Design, Manufacturing, Supply, Installation, Testing and Commissioning of SCADA compatible RMU having 7 Nos. 630A vacuum circuit breaker unit (one incomer and 6 outgoing) totally enclosed in 3mm Robotically welded & SF6 gas filled IP 66 grade stainless steel tank both side extensible with VPIS, end cap, motorized actuators for all ring switches and breaker unit, 24 V 26 AH battery, 230V, 5 A battery charger and 7 sets right angle boots & FPI including earth fault, over current and short circuit protection relay using relay for circuit breaker etc. IP 54 grade RMU outer shell shall be totally fabricated with 14 SWG Galvanize sheet with powder coated painting after 7 tank process as per standard. | No | 1 | 20,87,000 | 20,87,000 |
| 2 | Dismantling of existing 11 KV panel after demolishing of existing panel room wall etc. | No | 1 | 1,20,000 | 1,20,000 |
| 3 | Supply and providing of cable end termination for 3 C X 150 sq mm to 300 sq mm 11 KV cable including required additional sleeve etc complete | Nos. | 7 | 10,750 | 75,250 |
| 4 | Supply and providing of grilled rolling shutter in front of 11 KV panel room including civil work for the demolished wall etc complete for getting proper air ventilation. | LS |  | 75,000 | 75,000 |
| 5 | Supply and providing of MS channels and 6 mm chequered plate etc. for the RMU erection. | Kg | 350 | 150 | 52,500 |
| 6 | Supply and providing of 12 mm Rubber mat inside 11 KV panel room. | Nos. | 3 | 4600 | 13,800 |
| 7 | Supply and providing of first aid, shock treatment chart and as per Electrical Inspectorate standard | No | 1 | 750 | 750 |
| 8 | Supply and providing of 11 KV grade hand gloves | Pair | 1 | 700 | 700 |
| 10 | Inspection fee and Professional charges for getting approval and sanction order from Electrical Inspectorate for the replacing of the existing 11 KV panel with new panel | LS |  |  | 75,000 |
|  | Total |  |  |  | 25,00,000 |
|  | PMC charges |  |  |  | 2,00,000 |
|  | Grand total |  |  |  | 27,00,000 |
|  | Say Rs 27,00,000/- |  |  |  |  |

- Replacing of  existing 30 V, 40 Ah  battery bank for 1250 KVA No.2 transformer at SDF-17

Need & Necessity

The existing battery bank for control supply to No.2 transformer 1250 KVA at SDF-17 is old and its guaranty period is expired and hence required to replace the same. The estimate cost of 30 V, 40 Ah battery bank of No.2 Transformer control system at SDF-17 is Rs: 45,000/-

| Sl No | Particulars | Qnty | Rate | Amount( Rs) |
| --- | --- | --- | --- | --- |
| 1 | Supply installation Testing of 30 V, 40 Ah battery bank for 1250 KVA transformer No.2 at SDF-17 | 1 | 45,000 | 45,000.00 |

- Supply installation Testing & Commissioning of new 400 kWp Grid Tied Solar Power Plant

Need & Necessity

Minimum Solar RPO target fixed by KSERC for all Licensees for 2018-19 as per KSERC Renewable Energy Regulation 2017 are 2.75% of the total energy consumption. The total energy sale of CSEZA projected for during 2018-19 is estimated to be 55.49 MU. In order to meet solar RPO of 2.75%, solar generation of CSEZA required to be increased to 1.53MU for 2018-19. The present Solar Energy production from the existing 636 kWp CSEZ solar plants is 0.93 MU/annum and RPO coverage from the existing CSEZ Solar Plant is only 1.68%. This is in sufficient to meet the required minimum Solar RPO of 2.75 % for 2018-19. Hence, in order to meet the minimum solar RPO ,additionally 0.594 MU  solar power generation is required for the remaining 1.07%  solar RPO .Accordingly, CSEZA plans to install a 400 kWp Solar PV Plant incurring Rs.236 lakh as next phase.

| Estimate for Installation of new 400 kWp Grid Tied Solar Plant |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SL.No | Description | Unit | Qty | Rate (Rs) | Amount ( Rs) |
| 1 | Supply, Installation construction, erection and commissioning of 400 kWp. Grid-Tied Solar Power Plant Complete after conducting necessary survey before commencement of work including obtaining Electrical Inspectorate scheme and energisation approval after completion of work etc. | Kwp | 400 | 55,000 | 2,20,00,000 |
|  | Total |  |  |  | 2,20,00,000 |
|  | PMC Charge |  |  |  | 15,40 ,000 |
|  | Grand total |  |  |  | 2,35,40,000 |

Specification and break-up of the above estimate is given below:

| Sl No | Particulars | Qty | Amount |
| --- | --- | --- | --- |
| 1 | Solar PCU 50 KWp | 8Nos | 2,00,00,000 |
| 2 | Solar PVU 315 W | 1270 Nos |  |
| 3 | Cable and other accessories | Lot |  |
| 4 | AC/ DC Panels IP 65 with Protective Devices |  |  |
| 5 | Lightning arrestors |  |  |
| 6 | Earthing set |  |  |
| 7 | Monitoring System |  |  |
| 8 | Solar Energy Meter |  |  |
| 9 | Hot dipped Structural cost & Solar Meter room |  | 20,00,000 |
| 10 | Electrical Inspectorate Charges and Other expenses |  | 1,50,000 |
| 11 | PMC Charges |  | 15,40 ,000 |
| 12 | Grand Total |  | 2,35,40,000 |

- Supply, Installation, testing and Commissioning of 2 Nos 110kV, 31.5kA, 800A triple pole, centre post rotating, horizontal double break isolator without earth switch in 110 KV Substation Metering side.

Need & Necessity

CSEZA 110 kV substation have 8 nos. 110 KV yard isolators out of which 2 Nos isolators are frequently causing mechanical troubles and misalignment resulting 110 KV supply interruption at many times.  CSEZA receives 10 KV supply from two 100 KV feeders from KSEBL. These two isolators are installed in the 110 KV incoming 110 KV supply side and changing over of incoming are frequently required as per the request of KSEB during their Line maintenance work. Existing one set 110 KV line isolators on the No.1 feeder is now defective due to its contact worn-out. Hence it is proposed to procure two nos. new 110kV, 31.5kA, 800A triple pole, centre post rotating, and horizontal double break isolator without earth switch, upright mounting with Motor Operating Mechanism required to replace the defective isolators and to give uninterrupted supply to CSEZ consumers. The total estimate cost for the same is  Rs: 9, 29,880/-

| Estimate for Supply, Installing, Testing and Commissioning of 110kV, 31.5kA, 800A triple pole, centre post rotating, horizontal double break isolator without earth switch |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of 110kV, 31.5kA, 800A triple pole, centre post rotating, horizontal double break isolator without earth switch, upright mounting with Motor Operating Mechanism (made of MS sheet) for main switch ie., mechanically ganged with all accessories required for normal operation, but without support insulators, without supporting structure without terminal connectors with following configuration (for COPPER Design.) For 800A Without Earth Switch | Set | 2 | 1,82,500 | 3,65,000 |
| 2 | Supply of a set of 9 stacks consisting of One basic unite of 110 KV Solid core Insulators for a Bill of 550 KV having creep age distance of 3075 mm and cantilever strength of 6 KN ,as manufactured & tested by our Reputed suppliers | Set | 2 | 1,45,000 | 2,90,000 |
| 3 | Installation, Testing and Commissioning of 110kV, 31.5kA, 800A triple pole, centre post rotating, horizontal double break isolator without earth switch and unite of 110 KV Solid core Insulators | Set | 2 | 1,03,000. | 2,06,000 |
|  | Total |  |  |  | 8,61,000 |
|  | PMC charges |  |  |  | 68,880 |
|  | Grand total |  |  |  | 9,29,880 |

- Providing RTU panel in 110 kV Substation, for Open Access to CSEZA

Need & Necessity

As per KSERC Open Access Regulations, one time registration from SLDC is required   for obtaining open access consent. Necessary Remote Terminal Unit is also mandatory and to be installed in 110 KV Substation. CSEZA had already provided other requirements for open access such as connectivity, ABT compliant meters, CTs & PTs etc. to facilitate Open Access. Installation of remote terminal unit (RTU) is now essential to complete prerequisite and to proceed with open access consent for power procurement of additional 3 MVA and thereby reducing the existing tariff rate of CSEZA consumers. The Estimate cost is Rs: 4, 47,120/-.

| Estimate for providing RTU panel in 110 kV Substation |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| SL.No | Description | Unit | Qty | Rate in Rs | Amount (Rs) |  |
| 1 | Supply of fully wired RTU (Remote Terminal Unit) Panel. Enclosure-Powder Coated CRCA sheet steel of min. thickness 2mm.The Panel shall be floor mounted, with suitable base frame and detachable gland plates. The panel enclosure shall be suitable for installation inside the substation with protection class IP 44 or above with tamper proof locking facility, cooling fans for heat dissipation and other requirements as in the RTU specification provided by KSEB. | No | 1 | 3,50,000.00 |  | 3,50,000.00 |
| 2 | Charges for, Installation Testing , Commissioning of Remote Terminal Unit wired Panel (RTU), establishing communication with BSNL MPLS Modem in coordination with SLDC | No | 1 | 32,000.00 |  | 32,000.00 |
| 3 | Supply, wiring in surface/recessed mounted 20mm/25 mm PVC conduit with all accessories, using 2.5 sq.mm FRLS PVC insulated stranded copper conductor single core wire. Including supply and laying of 20mm/25 mm PVC conduit. | LS | 1 | 32,000.00 |  | 32,000.00 |
|  | Sub Total |  |  |  |  | 4,14,000.00 |
|  | PMC Charges |  |  |  |  | 33,120.00 |
|  | Grand Total |  |  |  |  | 4,47,120.00 |

- Procurement of 3G/4G GPRS Modem for Web Enabled Pre-paid Energy Metering System.

Need & Necessity

As stated under Sl No. (1) of capital works proposed for 2018-19, it is proposed to replace existing modems with high speed modems in phased manner. Accordingly it is proposed to procure 25 No’s of new 3G/4G GPRS modem  with an estimated amount of Rs. 4,00,000/- as next phase..

| Estimate for purchasing of 3G GPRS Modem for Web Enabled Pre-paid Energy metering System |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of 3G GPRS Modem (Model No. F2414- Four Faith Make) for Web Enabled Energy Monitoring System in CSEZ, Kakkanad. | Nos | 25 | 16,000. | 4,00,000 |
|  | Grand total |  |  |  | 4,00,000 |

Details of Capital works planned for 2020-21.

- Purchasing of 10 Nos Energy Meter for Power Distribution System in CSEZ

Need & Necessity

As detailed in  S.No 7 of  capital works proposed for the year 2018-19,. It is proposed to procure10 nos. of pre-paid energy meters in order to have adequate spare meters to cover meter failure and to ensure the new service connections are to be given in time. The total estimate cost is Rs 2, 43,540/-.

| Purchasing of Power and energy Meter for CSEZA Power Distribution System |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of Power and Energy Meter (Model No. Power logic ION 6200 Schneider Electric Make) for Power Distribution System in CSEZ, Kakkanad. | Nos | 10 | 24354 | 243540 |

- Purchasing of 1 No. 11KV / 0.415 KV 500 KVA USS Transformer as spare in Power distribution system.

Need & Necessity

CSEZA Power distribution systems have 8 nos of 11KV/433V power distribution transformers of various capacities up to 1250 KVA. In order to meet emergency backup supply to the consumers during transformer failure, a spare transformer is required. Hence it is proposed to procure one No 500 KVA trolley mounted Unitized transformer with an estimated amount of Rs 8, 00,000/-

| Purchasing of Power and energy Meter for Power Distribution System |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of 1 No. 11KV / 0.415 KV 500 KVA trolley mounted unitized Transformer | Nos | 1 | 8,00,000 | 8,00,000 |

- Procurement of 3G/4G GPRS Modem for web Enabled Pre-paid Energy Metering System.

Need & Necessity

As stated in Sl No.(1)  of capital works proposed for 2018-19,  it is proposed to procure 25 No’s of new 3G/4G GPRS modem  as next  phase  with an estimated cost of Rs 425000/-.

| Estimate for purchasing of 3G GPRS Modem for Web Enabled Pre-paid Energy Metering System |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of 3G GPRS Modem for Web Enabled Energy Monitoring System | Nos | 25 | 17,000 | 4,25,000 |

Details of Capital Works Planned for 2021-22.

- Replacing of existing old 30 V, 40 Ah control system battery bank of No.1 transformer installed at SDF-17

Need & Necessity

The existing battery bank for control supply to No.1 transformer 1250 KVA at SDF-17 is old and its guaranty period is expired and hence required to replace the same. The estimate cost of 30 V, 40 Ah battery bank for control system of 1250 KVA No.1Transformer   at SDF-17 is Rs: 45,000/-

| Sl No | Particulars | Qty | Rate | Amount |
| --- | --- | --- | --- | --- |
| 1 | Supply installation Testing of 30 V, 40 Ah battery bank for control supply of 1250 KVA transformer No.1 at SDF-17 | 1 | 45,000 | 45,000 |

- Replacing of existing old 30 V, 40 Ah battery bank for control system of distribution transformer at SDF-43.

Need & Necessity

The existing battery bank for control supply to 1250 KVA transformer at SDF-43 is old and its guaranty period is expired and hence required to replace the same. The estimate cost of 30 V, 40 Ah battery bank of Transformer control system at SDF-43 is Rs: 45,000/-

| Sl No | Particulars | Qnty | Rate | Amount |
| --- | --- | --- | --- | --- |
| 1 | Supply installation Testing of 30 V, 40 Ah battery bank for control supply of 1250 KVA transformer at SDF-43 | 1 | 45,000 | 45,000 |

- Purchasing of 10 Nos Energy Meter for Power Distribution System in CSEZ

Need & Necessity

As detailed in sl. No 7 of capital works proposed for 2018-19,it is proposed to  procure10 nos. pre-paid energy meters as next phase  .The total estimate cost  for the is Rs3,00,000/-.

| Purchasing of Power and energy Meter for Power Distribution System in CSEZ, Kakkanad. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of Power and Energy Meter (Model No. Power logic ION 6200 Schneider Electric Make) for Power Distribution System in CSEZ, Kakkanad. | Nos | 10 | 30,000. | 3,00,000 |

- Purchasing of 25 No’s of 3G /4G modem for the Web enabled Pre-paid Metering System

Need & Necessity

As detailed in Sl No.(1) of capital works proposed for 2018-19,it is proposed  to procure  25 No’s of new 3G/4G GPRS modem s as next phase with an estimated cost of Rs 425000/-.

| Estimate for purchasing of 3G GPRS Modem for Web Enabled Pre-paid Energy Metering System |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of 3G GPRS Modem for Web Enabled Energy Monitoring System | Nos | 25 | 17,000. | 4,25,000 |
|  | Grand total |  |  |  | 4,25,000 |

- Supply of 2 Nos 110 KV.800 A triple pole Isolators for EHT maintenance as spare in 110 KV substation.

Need & Necessity

CSEZA 110 kV substations have 8 nos. 110 KV yard isolators and some of these isolators are showing mechanical troubles and misalignment, resulting in 110 KV supply interruption... Hence it is proposed to procure two nos. new 110kV, 31.5kA, 800A triple pole, centre post rotating, and horizontal double break isolators as spare, to meet the emergency and to ensure un interrupted supply to CSEZ consumers. The total cost estimated for the same is Rs: 5, 94,000/-.

| Estimate for Supply of 110kV, 31.5kA, 800A triple pole, centre post rotating, horizontal double break isolator without earth switch in 110 KV Substation. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of Items | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| 1 | Supply of 110kV, 31.5kA, 800A triple pole, centre post rotating, horizontal double break isolator without earth switch, upright mounting with Motor Operating Mechanism (made of MS sheet) for main switch ie., mechanically ganged with all accessories required for normal operation, but without support insulators, without supporting structure without terminal connectors with following configuration (for COPPER Design.) For 800A Without Earth Switch | Set | 2 | 2,00,000. | 4,00,000 |
| 2 | Supply of a set of 9 stacks consisting of One basic unite of 110 KV Solid core Insulators for a Bill of 550 KV having creep age distance of 3075 mm and cantilever strength of 6 KN ,as manufactured & tested by our Reputed suppliers | Set | 1 | 1,50,000. | 1,50,000 |
|  | Total |  |  |  | 5,50,000 |
|  | PMC charges |  |  |  | 44,000 |
|  | Grand total |  |  |  | 5,94,000 |