(A Government of India Enterprise)

New Administrative Building,

Willingdon Island, Cochin-682009, Kerala

Tel: 0484–2666639, 2582300, 2582305

Fax: 0484–2666639

E mail :cme@cochinport.gov.in

Website: www.cochinport.gov.in

E-TENDER DOCUMENT

For

Request for Selection (RFS) of Bidders for the

Implementation of 1.5 MWp Grid connected Floating Solar PV Project with Battery Energy Storage System at Willingdon Island, Cochin Port Authority including Operation and Maintenance for 25 years under RESCO model

TABLE OF CONTENTS

| DESCRIPTION | PAGE NO. |
| --- | --- |
| SECTION - I : Invitation for Bids (IFB) | 4 -11 |
| SECTION - II : Instructions to Bidders (ITB) | 12 -42 |
| SECTION - III : Qualifying Requirements (QR) | 43-44 |
| SECTION - IV : Definitions of Terms | 45-49 |
| SECTION - V : Bid Evaluation and Selection ofProjects | 50-53 |
| SECTION - VI : Other Provisions | 54-55 |
| SECTION - VII : Sample Forms & Formats for Bid Submission | 56-94 |
| ANNEXURE - A : Technical Requirements for Grid Connected Floating Solar Power Projects | 95-117 |
| ANNEXURE - B : Check List for Bank Guarantees | 118 |
| ANNEXURE - C : List of Banks | 119-120 |
| ANNEXURE - D : Special Instructions to Bidders for e- Tendering and Reverse Auction | 121-122 |
| ANNEXURE - E : Terms & Conditions of Reverse Auction | 123-125 |
| ANNEXURE - F : Guidelines issued by Govt. of Kerala for the installation of Solar Energy system | 126-129 |

DISCLAIMER

Though adequate care has been taken while preparing the RFS document, the bidder(s) shall satisfy themselves that the document is complete in all respects. Intimation regarding any discrepancy shall be given to the office of Employer/Owner immediately. If no intimation is received from any bidder within 20 (Twenty) days from the date of issuance of RfS documents, it shall be considered that the document is complete in all respects and has been received/ acknowledged by the bidder(s).

Cochin Port Authority (CoPA) reserves the right to modify, amend or supplement thisdocument.

While this RfS document has been prepared in good faith, neither Cochin Port Authority nor their employees or advisors make any representation or warranty, express or implied, or accept any responsibility or liability, whatsoever, in respect of any statements or omissions herein, or the accuracy, completeness or reliability of information, and shall incur no liability under any law, statute, rules or regulations as to the accuracy, reliability or completeness of this document, even if any loss or damage is caused by any act or omission on their part.

Place: Kochi										Date:

SECTION-I

INVITATION FOR BIDS (IFB)

FOR

Selection of Solar Power Developers for “Implementation of 1.5 MWp Grid connected Floating Solar PV Project with Battery Energy Storage System at Willingdon Island, Cochin Port Authority, including Operation and Maintenance for 25 yearsunder RESCO model”

The tender is invited in two cover system from experienced manufacturers / EPC contractors through Government e-marketplace (the GeM portal). For submitting the e-tender, the prospective bidders willing to participate in this tender are required to get registered with Government e Market place (GeM).Tender timeline is available in the BID INFORMATION SHEET given in the tender document.

(SINGLE STAGE TWO COVER BIDDING)

under e-Tendering through GeM

1.0	Cochin Port Authority, Cochin (formerly Cochin Port Trust), a Body Corporate under the Major Port Authorities Act, 2021, (hereinafter called “CoPA”) is an Autonomous body under the Ministry of Ports, Shipping and waterways (MoPSW). Cochin Port Authority has to comply with the Ministry’s directions in implementing and facilitating Green Port Initiative for development, and promotion of solar energy technology. More over CoPA is a Deemed Distribution Licensee for electricity in Port area at W. Island and Vallarpadam & Puthuvypin as per Electricity Act2003. CoPA has to comply with the Renewable Power Obligations in accordance with KSERC (Renewable Energy and Net Metering Regulations) 2020/ 2022

2.0	As part of the Government of India’s target of achieving a cumulative capacity of 100 GW Solar PV installation by the year 2022 and for transforming 60% of power usage in Major Ports to renewable energy by the year 2030 in accordance with Maritime India Vision 2030 (MIV 2030), Cochin Port Authority (CoPA) wishes to invite proposals for  setting up of grid connected Floating Solar Power Projects to be installed at in the  Backwaters near CoPA’s Walkway Avenue  between BOT Junction and Kannangatt bridge at W/Island, Cochin, Kerala, on BOOT (Build Own Operate Transfer)/ RESCO basis for an aggregate capacity of 1.5 MWp. Cochin Port Authority (CoPA) shall enter into Power Purchase Agreement (PPA) with the Solar Power Developer within 90 ( ninety) days from the date of LoA or within one month from approval of PPA by KSERC.

OVERVIEW OF THE RfS

3.0	Solar Power Developer (herein after referred to as SPDs) selected by CoPA based on this RfS, shall conduct Site Survey, Design, obtain Statutory Approvals, Engineering, Manufacture, Supply, Storage, Civil work, Erection, obtain CEA approval, Testing & Commissioning of 1.5 MWp Grid Connected Floating Solar PV Project with suitable BESS based on the load data provided by CoPA, in the Backwaters near CoPA’s Walkway Avenue between BOT junction and Kannangatt bridge at W/Island, Cochin Port Authority, Kerala, generated Power Transmission to 11kV grid of Port’s 110kV substation at Willingdon Island, including Operation & Maintenance (O & M) of the project for a period of 25 (Twenty Five) Years under BOOT/ RESCO Model after Operational Acceptance” in accordance with the provisions of this RfS document and Power Purchase Agreement (PPA).

4.0	The Cochin Port Authority (CoPA) shall enter into PPA with selected SPD within 90 ( ninety) days from the date of LoA or within one month from approval of PPA by KSERC for a period of 25 years from the date of commercial operation of the project. The maximum tariff payable to the Project Developer will be fixed/approved by the KSERC after the bidding process. The Bidders will be free to avail fiscal incentives like Accelerated Depreciation, Concessional Customs and Excise Duties, Tax Holidays if available and at the responsibility of SPDs and the bidders shall note that the concessions in the duties cannot be claimed as a right for increase in tariff later on and whatever tariff quoted and approved by KSERC will be final. The price quoted by the bidder shall be provisional and subjected to change as per the approval of the Kerala State Regulatory Commission (KSERC).

5.0	Bidders shall submit their bid by offering a single tariff which shall be applicable during the entire operation and maintenance period of 25 years.  There shall not be any upward revision in the approved tariff.

6.0	No transfer or selling of the plant to the third party is allowed during PPA period without the consent of CoPA and without remittance of necessary fees to CoPA as applicable. If the Project is transferred or                                                     sold to a third party during its tenure after commercial operation, CoPA reserves the full right to operate the Solar plant with the other SPD at its discretion.

SELECTION OF TECHNOLOGY & ELIGIBLE PROJECTS UNDER THIS RFS

7.0	The Projects to be selected under this RfS for aggregate capacity of 1.5MWp with suitable BESS designed based on the load data for the last 5 years provided by CoPA, are to be provided for implementation of Floating Solar PV Projects and are to be installed in the Backwaters near the CoPA’s Walk way Avenue between BOT junction and Kannangatt Bridge at W/Island, Kochi, Kerala, India. The selection of solar PV modules should be of the latest technology prevailing in the market to withstand humidity levels and high moisture ingress prevailing in this area. The PV modules shall comply with the latest technology and high efficiency as per MNRE /BIS standards.  Modules used shall have proven design and demonstrated performance. BIS/ MNRE standard shall be used for anchoring/ mooring of the PV floating panel also.

GENERAL

8.0	The Invitation for Bids is open to all eligible bidders meeting the Minimum Qualification Criteria. The complete RfS Documents are available in the GeM portal https://gem.gov.in/, in the CoPA website www.cochinport.gov.in as well as in the Central Public Procurement Portal of Govt. of India, www.eprocure.gov.in . Interested bidders shall download the RfS Documents from these portals as per the provisions available therein. Tenders attaching all documents shall be submitted through GeM portal strictly in accordance with the instructions to bidders (ITB), terms and conditions of the tender document, before the tender submission time mentioned in the tender.

9.0	Interested bidders have to necessarily register themselves in the GeM portal to participate in the tender. For proper uploading of the bids on the portal namely https://gem.gov.in/ (hereinafter referred to as the ‘portal’), it shall be the sole responsibility of the bidders to appraise themselves adequately regarding all the relevant procedures and provisions as detailed in the portal as well as by contacting GeM, through e-mail to: helpdesk-gem@gov.in  or call on Toll Free Numbers (Inbound): 1-1800-419-3436/ 1-1800-102-3436 (9:00am-6:00pm Mon to Sat) Help Desk Out bound No's: +911244875125 & +917556685120, as and when required, contact details are also mentioned on the Bid Information Sheet. The Employer in no case shall be responsible for any issues related to timely or properly uploading/ submission of the bid in accordance with the relevant provisions of Section II - ITB of the Bidding Documents.

10.0	A Single Stage Two Cover Bidding Procedure with Earnest Money Deposit (EMD) will be adopted and will proceed as detailed in the RfS Documents.

11.0	Bidders should submit their bid proposal online complete in all aspects on or before last date and time of Bid Submission as mentioned on Portal of GeM (https://gem.gov.in/ ) and as indicated in the Bid Information Sheet.

12.0	(i) Bidder shall submit bid proposal along with Earnest Money Deposit (EMD), complete in all respects as per the Bid Information Sheet. Techno-Commercial bids will be opened online in the GeM Portal. Bid proposals received without the prescribed Earnest Money Deposit (EMD)/Documents for exemption of EMD will be considered as non-responsive. In the event of any date indicated is a declared Holiday, the tender will be opened on the next working day.

(ii)Bank details of Cochin Port Authority are as follows: State Bank of India, Cochin Port Authority Branch, IFSC Code: SBIN0006367, Account No. 10601197375.

(iii)  Exemption from the payment of EMD and Cost of Tender document shall be given to Micro and Small Enterprises (MSEs) as defined in MSE Procurement Policy issued by Department of Micro, Small and Medium Enterprises (MSME) or are registered with the Central Purchase Organization or the concerned Ministry or Department as provided in GFR 2017. In this regard the firm should submit valid certificate.

13.0	RfS documents which include Eligibility Criteria, Technical Specifications, various Conditions of Contract, Formats etc. can be downloaded from GEM Portal (https://gem.gov.in/) or from CoPA website (http://www.cochinport.gov.in) or Central Public Procurement Portal of Govt. of India, www.eprocure.gov.in,. Any amendment(s)/ corrigendum(s)/ clarification(s) with respect to this RfS shall be uploaded on the above mentioned websites only and no intimation will be sent to the individual bidders. The Bidder should regularly check for any Amendment(s)/ Corrigendum(s)/ Clarification(s) on the above mentionedwebsite.

14.0	The detailed Qualifying Requirements (QR) are given in Section-III of the RfS.

16.0	CoPA shall conduct Reverse Auction, if required or as per provisions of RfS documents. The decisions of CoPA will be final in this regard and binding to all bidders.

17.0	The bidders have to execute an “Integrity Pact”(IP) as per the format available in the CoPA’s website www.cochinport.gov.in. The Tenderer should sign and upload the “Integrity Pact” duly signed in all the pages duly affixing the firm’s seal.

The Independent External Monitors (IEM) for Cochin Port are as follows:

1) 	Shri. M J Joseph, ICAS (Rtd.)

37, Da Costa Square

3rd Cross, Cooke Town

Bangalore – 560 084

Email:  joseph.iem@cochinport.gov.in

2) 	Shri. Punati Sridhar, IFoS( Retd)

8C, Block -4, 14-C Cross,

MCHS Colony, HSR 6th Sector,

Bangalore -560102

Email ID : sridhar.iem@ cochinport.gov.in

18.0	The bidder should not have been blacklisted or debarred by any Central/ State Government Agency of Central/State Government/Public Sector Undertaking/ Regulatory Authority of India at the time of submission of this bid.

#### 19.0	CoPA reserves the right to cancel/ withdraw this invitation for bids without assigning any reason and shall have no liability whatsoever consequent upon such a decision.

#### 20.0	Electrical works should be carried out through a licensed Electrical contractor since clearance has to be obtained from the Central Electricity Authority (CEA).  The Electrical contractor engaged by the SPD shall hold valid “A-Class” license.  A copy of the license shall be submitted along with tender or furnish an undertaking that the SPD shall tie-up with a contractor having A class Electrical license in the case of award contract.

#### 22.0	All the statutory clearances shall be obtained for setting up of the Floating solar plant in the water body.

INTERPRETATIONS

- Words comprising the singular shall include the plural & vice versa.

- An applicable law shall be construed as reference to such applicable law including its amendments or re-enactments from time to time.

- A time of day shall save as otherwise provided in any agreement or documents construed as a reference to Indian Standard Time.

- Different parts of this contract are to be taken as mutually explanatory and supplementary to each other and if there is any differentiation between or among the parts of this contract, they shall be interpreted in a harmonious manner so as to give effect to each part.

- The table of contents and any headings or sub headings in the contract has been inserted for case of reference only & shall not affect the interpretation of this agreement.

BID INFORMATION SHEET

The brief details of the RfS are as under:

| A | RfS NO. & DATE | F1/T- / Floating Solar- /2022/M dated 00/00/2022 |
| --- | --- | --- |
| B | Document Description | Implementation of 1.5MWp grid connected floating solar PV power plant for Cochin Port Authority under RESCO model. |
| C | NAME OF WORK/ BRIEF SCOPE OF WORK/ JOB | Selection of Solar Power Developer to obtain PPA approval, Site Survey, obtain Statutory approvals from Govt. bodies & KSEBL, approval by KSERC etc., Design, Engineering, Manufacture, Supply, Storage, Civil work, Erection, TPIA inspection, CEA approval, Testing and Commissioning of 1.5MWp Grid Connected Floating Solar PV Project with suitable BESS based on load data provided by CoPA, in the Backwaters near CoPA’s Walkway Avenue between BOT Junction and Kannangatt bridge at Willingdon Island, Cochin, Kerala, generated Power transmission to 11kV grid inside 110kV substation of CoPA at Willingdon Island, including Operation & Maintenance (O & M) of the project for a period of 25 (Twenty Five) Years under RESCO Model BOOT, after Operational Acceptance. |
| D | ESTIMATED VALUE | Rs.6,25,50,000/- The estimated cost of the project excludes the cost of BESS, cost of cables and other switch gears required for connecting the Solar Plant to the 110 KV SS located at Willingdon Island approximately at a distance of 3.5 KM from the project location. |
| E | TYPE OF BIDDING SYSTEM | E-TENDER through GeM portal (https://gem.gov.in/) |
| F | TYPE OF RfS/ TENDER | Single stage 2 cover system with EMD |
| G | COMPLETION/ CONTRACT PERIOD | As mentioned in RfS Documents [Reference Clause No. 16, Section-II, Instructions to Bidders (ITB) of RfS] |
| H | BID PROCESSING FEE (NON-REFUNDABLE) | Not applicable since bidding is through GeM |
| I | Bid Bond / EARNEST MONEY DEPOSIT (EMD) | Amount: INR 6,25,500/- (Indian Rupees Six Lakhs Twenty Five Thousand Five hundred only) (EMD shall be furnished in the form of Account Payee Demand Draft/ Banker’s Cheque/ Fixed Deposit Receipt /Bank Guarantee from a Commercial Bank in favour of “FA&CAO, Cochin Port Authority”, payable at Cochin or online payment in an acceptable form safeguarding the purchaser’s interest in all respects). The exemption shall be granted as per GFR 2017. |
| J | PERFORMANCE BANK GUARANTEE (Security Deposit) | As per Tender Document (Security Deposit shall be furnished in the form of Account Payee Demand Draft/ Banker’s Cheque/ Fixed Deposit Receipt /Bank Guarantee from a Commercial Bank in favour of “FA&CAO, Cochin Port Authority”, payable at Cochin or online payment in an acceptable form safeguarding the purchaser’s interest in all respects |
| K | DATE, TIME & VENUE OF PRE-BID MEETING | As per NIT on GEM portal |
| L | ONLINE BID-SUBMISSION DEADLINE DATE | As per NIT on GEM portal |
| M | TECHNO- COMMERCIAL BID OPENING | As per NIT on GEM portal, at the Office of the Chief Mechanical Engineer, 1st Floor, New Administrative Building, Cochin Port Authority, Cochin 9. |
| N | PRICE BID OPENING | Date and time will be informed later to the eligible bidders. |
| O | CONTACT DETAILS OF GEM | Mail at: helpdesk-gem@gov.in |
| P | NAME, DESIGNATION, ADDRESS AND OTHER DETAILS (FOR SUBMISSION OF RESPONSE TO RFS) | The Chief Mechanical Engineer, Cochin Port Authority, 1st floor, New Administrative Building, W/Island, Kochi-9 Tel. 0484-2666639, 2582300, 2582305 Fax:- 0484-2666639 Email : cme@cochinport.gov.in |
| Q | DETAILS OF PERSONS TO BE CONTACTED IN CASE OF ANY ASSISTANCE REQUIRED | - Shri. V. Thuraipandian, CME Ph: 0484-2666639, 2582300 - Smt. Ajithkumar D., EE (Ele)P Ph: 0484-2582320 - Sri. Ajayakumar R.S., EE(Ele.) Ph: 0484-2582305/07 |

Note:

- Bids must be submitted strictly in accordance with Section-II, Instructions to Bidders (ITB) depending upon Type of Tender as mentioned at Clause no.(D) of Bid Information Sheet. The ITB is an integral part of the RfS document.

- Any bidder, who meets the Qualifying Requirement and wishes to quote against this  RfS, may download the complete RfS document along with its amendment(s) if any from the Portal of GEM (https://gem.gov.in/)and/ or CoPA website (www.cochinport.gov.in) or Central Public Procurement Portal of Govt. of India www.eprocure.gov.in and submit their Bid complete in all respects as per terms & conditions of RfS Document on or before the due date of bid submission. Clarification(s)/ Corrigendum(s) if any shall also be available on above referred websites.

- Prospective Bidders are requested to remain updated for any notices/ amendments/ clarifications etc. to the RfS document through the website https://gem.gov.in/. No separate notifications will be issued for such notices/ amendments/ clarifications etc. in the print media or individually. Intimation regarding notification on the above shall be updated on www.cochinport.gov.in, https://gem.gov.in/aswell as on Central Public Procurement Portal of Govt. of India, www.eprocure.gov.in .

SECTION - II

INSTRUCTIONS TO BIDDERS (ITB)

TABLE OF CONTENTS

- OBTAINING RfS DOCUMENTS

- COST OF DOCUMENTS/ PROCESSINGFEE

- TOTAL CAPACITY OFFERED

- PROJECT LOCATION

- PROJECT SCOPE & TECHNOLOGY SELECTION

- MAXIMUM ELIGIBILITY FOR PROJECT CAPACITY ALLOCATION FOR A BIDDER

- CONNECTIVITY WITH THE GRID

- POWER GENERATION BY SOLAR POWER DEVELOPER

CRITERIA FORGENERATION

SHORTFALL IN GENERATION

EXCESS GENERATION

OFFTAKE CONSTRAINTS DUE TO TRANSMISSION INFRASTRUCTURE/ GRID UNAVAILABILITY & BACKDOWN

- CLEARANCES REQUIRED FROM THE STATE GOVERNMENT AND OTHER LOCAL BODIES

- EARNEST MONEY DEPOSIT (EMD)

- PERFORMANCE BANK GUARANTEE (PBG)

- SUCCESS CHARGES

- FORFEITURE OF EMD

- POWER PURCHASE AGREEMENT (PPA)

- FINANCIAL CLOSURE OR PROJECT FINANCING ARRANGEMENTS

- COMMISSIONING

PARTCOMMISSIONING

COMMISSIONING SCHEDULE AND LIQUIDATED DAMAGE FOR DELAY IN COMMISSIONING

EARLYCOMMISSIONING

- COMMERCIAL OPERATION DATE (COD)

- MINIMUM PAID UP SHARE CAPITAL TO BE HELD BY PROJECT PROMOTER

- STRUCTURING OF THE BID SELECTION PROCESS

- INSTRUCTIONS TO BIDDERS FOR STRUCTURING OF BID PROPOSALS IN RESPONSE TORfS

- IMPORTANT NOTES AND INSTRUCTIONS TOBIDDERS

- NON-RESPONSIVE BID

- METHOD OF SUBMISSION OF RESPONSE TO RfS BYTHEBIDDER

DOCUMENTS TO BE SUBMITTED OFFLINE (IN ORIGINAL)

DOCUMENTS TO BE SUBMITTED ONLINE

- NOTICE BOARD FOR DISPLAY

- VALIDITY OF THE RESPONSE TO RfS

- BID PREPARATION COST

- CLARIFICATIONS/ PRE BID MEETING/ ENQUIRIES/AMENDMENTS

- RIGHT OF COPA TO REJECT A BID

- POST AWARD COMPLIANCES

- OWNERSHIP OF THE PLANT AFTER 25 YEARS

Preamble

This part (Section - II) of the RfS Documents provides the information necessary for bidders to prepare responsive bids, in accordance with the requirements of the Employer. It also provides information on bid submission and uploading the bid on GeM portal (https://gem.gov.in/), bid opening, evaluation and onaward of contract. This Section (Section II) contains provisions that are to be used unchanged unless consists of provisions that supplement, amend, or specify in detail, information or requirements included in RfS and that are specific to each procurement, states otherwise.

Bidders may note that the respective rights of the Employer/ Owner and Bidders/ Contractors shall be governed by the RfS Documents/ Contracts signed between the Employer/ Owner and the Contractor for the respective package(s). The provisions of RfS Documents shall always prevail over any other documents in case of contradiction.

Further in all matters arising out of the provisions of this Section - II and the RfS Documents, the laws of the Union of India shall be the governing laws and courts of Kochi shall have exclusive jurisdiction.

### OBTAINING RfS DOCUMENTS

The RfS document can be downloaded from the Portal of GEM (https://gem.gov.in/).The same is also available at www.cochinport.gov.in and Central Public Procurement Portal of Govt. of India, www.eprocure.gov.in.

### Note: Interested Bidders have to download the official copy of RfS & other documents through registering in the GeM portal. The Bidder shall be eligible to submit/upload the bid only after obtaining approval in the respective service category and ample time shall be provided in anticipation to the process.

- COST OF RfS DOCUMENTS / PROCESSING FEES

### The Bid Processing Fee / Cost of RfS is not applicable since bidding is through GeM.

### Bidders who are registered with MSME/ NSIC/UAM under the Ministry of MSME and as per MSE procurement policy, Micro and Small Enterprises shall be eligible for exemption of EMD and tender document cost. They are required to submit documentary proof of such registration along with the offer, for claiming the available exemptions and a scanned copy of Exemption Certificate shall be uploaded in the GeM Portal along with the Technical bid.

- TOTAL CAPACITY OFFERED

  - Selection of Grid Connected Floating Solar Power Projects for total capacity of grid connected 1.5MWp (A.C.) shall be of any of the following sizes:

  - The project site shall be either a single module of 750 Mtrs long along the canal shore with 20 mtrs width towards water body (Total area 15000 Sqmtr) or 2 segments on both sides of small culvert each having 375 Mtrs long on both sides with 20 metres towards water body and so on.

  - The Project comprises “Selection of Solar Power Developer for the Site Survey, obtaining Statutory Approvals, PPA approval from KSERC, Design. Engineering, Manufacture, Supply, Storage, Civil work, Erection, CEA approval, Testing and Commissioning of 1.5MWp Grid Connected Floating Solar PV Project with Battery Storage Systems, in the Backwaters near CoPA’s Walkway Avenue between BOT junction and Kannangatt bridge at Willingdon Island, Cochin, Kerala, Transmission of solar Power upto 11kV grid of Port’s 110kV main receiving substation at Willingdon Island. The Project to be selected under this RfS including Operation & Maintenance (O & M) of the project for a period of 25 (Twenty Five) Years under RESCO Model (BOOT) after Operational Acceptance.”

  - CoPA’s Power purchase agreement with M/s KSEBL is for 6.5 MVA at 110kV level in Bulk supply tariff at W.Island. Average monthly consumption of CoPA is 21 lakh units at W. Island. Total power requirement of CoPA including its consumers at W.Island, is usually less than 2 MVA during low demand period and Sundays/ Holidays. CoPA   have already installed two solar power plants of capacity 100 KWP and 150 kwp respectively, in W.Island. (Total installed capacity =250 kWP). Earlier M/s KSEBL had rejected the request of grid connectivity by CoPA. Being a small distribution licensee, CoPA may not be able to evacuate the 100 % solar power generated on commissioning of the 1.5 MWp floating solar power plant. CoPA will take up the proposal for grid connectivity and solar power export to KSEBL’s grid with KSERC along with CoPA’s petition for PPA approval. If grid connectivity and solar export is not permitted by KSERC, excess solar power will have to be stored using adequate Battery Energy Storage System by the successful SPD, otherwise solar capacity will have to be reduced from 1.5 MWp as per the outcome of the petition. The bidders shall take into account of BESS / reduction of solar power capacity while quoting for the tender. The load pattern of CoPA for the last 5 years is attached for the analysis of the bidders in this regard.

  - The interested Bidders are required to participate in the Request for Selection (RfS) for installation of Grid Connected Floating Solar Photovoltaic Power Plants on Build-Own-Operate-Transfer (B-O-O-T)basis/ RESCO Model. The ownership of the project shall be transferred to Cochin Port Authority after completion of entire PPA period.

  - The bidder shall supply and lay 11 kV cables, supply and install necessary switchgears including VCB panels compatible to interface with SCADA  to connect the solar plant to the 11 kV grid of Cochin Port at 110 kV substation with necessary switchgears/ VCB panels, necessary protection relays, monitoring panels, metering arrangement etc. Any modifications of existing 11kV grid for enabling the connectivity is under contractor's scope. The bidder should ensure 1.5MWp at 11kV as per the standards. At the 11kV side, the AC output shall be 1.5MWp at standard test conditions.  The SPD shall provide  the connectivity at 110kV substation by providing suitable inverter transformers, 11kV cables, 11KV switch gears, metering equipments including meters (both solar meter and grid meter) etc and the SPD shall make all arrangements so that the power generated from the solar power project shall be brought to the existing 110kV substation of Cochin Port Authority, which is about 3.5km away from the substation at A2 area, complying with Central Electricity Authority  Regulations relating to Construction Standards, Technical Standards, Safety Regulations, Grid Connectivity and Communication and State Load Dispatch Centre (SLDC) norms. The SPD shall submit the bid considering the cost for all the above items. The metering shall be done in accordance with CEA Metering regulations /KSERC regulation/ KSEBL rules in the 11kV side through bidirectional meter 110kV substation with necessary switchgears/ Panels and solar meter at solar plant premises. In connection with the Project work, CoPA shall assist the SPD for getting statutory approvals from the statutory bodies. The documentation required for statutory approval and charges shall be done by the SPD.

The SPDs shall demonstrate the Contracted Capacity at the Interconnection Point, as defined in the Commissioning Procedure enclosed in Annexure-A and Appendix-A-1.

The Cochin Port Authority at its discretion reserves the right to award Repeat order to the successful Bidder / Solar Power Developer to  install additional capacity of 25% over and above the present requirement of 1.5 MWp Floating Solar project if the levelised tariff approved by the KSERC and accepted by the Successful Bidder / Solar Power Developer, is found reasonable compared to the Bench mark price for the Kerala Region as may be decided by KSERC and based on the performance of the Solar PV Plant installed by the Solar Power Developer for a period of one year. ie if the Cochin Port wants to install the Additional capacity Grid connected Floating Solar PV Project of a further capacity of 0.375 MWp, the SPD shall carry out the additional capacity plant at the same rates, terms and conditions.  The Bidders are requested to consider the above aspect while quoting the rates for the 1.5 MWp Floating Solar project.

PROJECT CONFIGURATION

The term “Project” shall have the meaning as defined in Section IV of the RfS, and shall refer to the cumulative Project capacity as quoted by/awarded to the Bidder.

The Bidder may however, set up the cumulative Project capacity at a single location, or he may configure the “Project” as being sub-divided into two numbers of “Packages”, being set up at multiple locations as approved by the Cochin Port Authority with due consideration of the following factors.

A single tariff shall be quoted by the Bidder for the entire Project, irrespective of the Project configuration and the tariff quoted is subject to approval by KSERC and shall be binding on the SPD. The tariff shall include all the costs related to Scope of Work. Bidder shall quote for the entire facilities on a “single responsibility” basis such that the total Bid Price covers all the obligations mentioned in the Bidding Documents in respect of Design, Supply, Erection, Testing and Commissioning including Warranty, Operation & Maintenance for a period 25 years under RESCO model, goods and services including spares required if any during O&M period. The Bidder has to take all permits, approvals and licenses, Insurance etc., provide training and such other items and services required to complete the scope of work mentioned above.

    - Power Purchase Agreement shall be executed within 90 days from the date of LOA or within 30 days from the approval of KSERC. PPA shall be executed complying with the orders of the Hon’ble Kerala State  Electricity Regulatory Commission. Draft PPA attached along with RfS shall be modified, if required in compliance with KSERC orders.

    - The entire Project shall have a single Effective Date of the PPA and single milestones for achieving Financial Closure and Commissioning, irrespective of the configuration of the Packages.

### PROJECT LOCATIONS

The Project(s) shall be located at the water body near CoPA’s walkway avenue, which is approx. 3.5km from the Port’s main 110kV receiving station. The SPD shall provide at his cost, required 11KV switch gears, transformers, transmission U.G cables etc. for interconnecting solar power to the Port’s grid. The project site shall be either a single module of 750 Mtrs long along the canal shore with 20 mtrs width towards water body (Total area 15000 Sqmtr) or 2 segments on both sides of small culvert each having 375 Mtrs long on both sides with 20 metres towards water body and so on.

A substantial portion of proposed location on either side of the culvert is covered through mangroves. Further the water body area near to the reclamation wall is currently very shallow and slushy for about 100 Mtr.

There is no lease or license will be levied by the Cochin Port Authority, being the project is for the self consumption, i.e., Cochin Port’s own project.

The geographic location of the backwaters of CoPT Walkway is as follows:

Latitude:0955.7NLongitude:07616.6E

Location:https://maps.google.com/?q=9.930979,76.279625;	EdakochiKayal (Kochi, Kerala, India): https://maps.google.com/?q=9.929129,76.277534 ;

NH966B(NH966B, Kochi682006, Kerala,India): https://maps.google.com/?q=9.928128,76.285858.

Quality parameters of water at the site is Saline.

Site survey, Bathymetric study, water body characteristics, geo-technical investigations (on shore/off shore) etc., water properties (such as TDS content etc), depth of reservoir (Full Reservoir Level (FRL), Minimum Drawdown level (MDDL), Dead Storage level etc.,), variation in the depth of water reservoir, water flow rate / current, climatic conditions have to be carried out after award of contract.

### PROJECT SCOPE & TECHNOLOGY SELECTION

Under this RfS, the SPD shall set up Floating Solar Power Project(s) with BESS, including the transmission and necessary infrastructure upto the Interconnection/Delivery Point in line with Clause No.7, Section-II, ITB, at its own cost and in accordance to the provisions of this RfS document. All approvals, permits and clearances required for setting up of the Project including those required from State Government and local bodies shall be in the scope of the SPD. The SPD appointed shall obtain necessary CRZ clearance for the project from the concerned authorities like NCESS, KCZMA  i.e Environmental clearance/Approval from statutory bodies and the Clearance from Pollution Control Board and other statutory bodies if any.  All the expenses for obtaining the statutory clearances shall be borne by the SPD.

The SPD shall be required to follow the applicable rules regarding project registration with the Regulatory bodies, as required, in line with the provisions of the applicable policies/ regulations of the State. It shall be the responsibility of the SPD to remain updated about the applicable charges payable to the Regulatory bodies under the State Solar Policy.

### MAXIMUM ELIGIBILITY FOR PROJECT CAPACITY ALLOCATION FOR A BIDDER

Following conditions shall be applicable to the Bidders for submission of bids against this RfS:

- A Bidder including its Parent, Affiliate or Ultimate Parent or any Group Company can submit only a single bid for the project in the prescribed formats as detailed in Clause No.20, Section-II, ITB, giving details of the Projects.

- The evaluation of bids shall be carried out as described in Section-V of RfS. The methodology for allocation of Projects is elaborated in Section-V of RfS.

### CONNECTIVITY WITH THE GRID

The Project should be designed for interconnection with the 11kV grid at CoPA’s 110kV main receiving substation in accordance with the prevailing CEA /KSERC regulations/ SLDC norms. For interconnection with the grid and metering, the SPD shall abide by the applicable Grid Code, Grid Connectivity Standards, Metering Regulations, Communication Regulations etc. (as amended from time to time) issued by  Appropriate Commission and Central Electricity Authority (CEA) and any other statutory body(ies).

  - The maintenance of Transmission system upto the Inter connection Point shall be the responsibility of the SPD.

  - The arrangement of connectivity can be made by the SPD through a dedicated transmission cable and 11 KV switch gears at their cost. The entire cost of transmission including cost of laying of cable, SLDC/ Scheduling charges, Security, MOC (Maintenance Operational Check), losses etc., if required and any other charges from the Project up to the Interconnection Point shall be borne by the SPD. The meters for the project at the interconnecting point at 11kV panel at 110 kV substation shall be sealed by CoPA.

  - Reactive power charges as per CERC/KSERC regulations shall be payable by SPD as per provisions of PPA.

  - Metering arrangement of project shall have to be adhered to in line with relevant clause of the PPA.

  - The Buying Utility (CoPA) will not be responsible for all transmission charges, reactive compensation charges of grid, losses and any other charges as applicable under the respective regulations / KSERC tariff orders for the 1.5 MWp solar power generation. The above charges shall be payable by the SPD.

### POWER GENERATION BY SOLAR POWER DEVELOPER

  - Criteria For Generation

The annual Capacity Utilization Factor of Solar PV project shall be 21% as per the KSERC (RE & Net metering) Regulations 2022, fixed for the solar PV projects or as revised by the Kerala State Electricity Regulatory Commission from time to time.

The successful bidder shall be required to meet minimum guaranteed generation with Performance Ratio (PR) at the time of commissioning and related Capacity Utilization Factor (CUF) during the O&M period of 25 years as stipulated by the KSERC Regulations from time to time. It shall be the responsibility of the SPD, entirely at its cost and expense to install such number of Solar panels and associated equipment as may be necessary to achieve the required CUF, and for this purpose SPD shall make its own study and investigation of the GHI (Global Horizontal Irradiance) and other factors prevalent in the area which have implication on the quantum of generation. SPD shall maintain generation so as to achieve annual CUF of 21%  or as revised by the Kerala State Electricity Regulatory Commission from time to time, till the end of 25 years from COD (Commercial Operation Date).  The annual CUF will be calculated every year from 1stApril of the year to 31stMarch next year. The CUF for the period between COD/commencing date upto 1st April (if any) and 31st March upto final closing date (if any) shall be calculated on pro-rata basis.

### Shortfall In Generation

If for any Contract Year, it is found that the SPD has not been able to generate minimum energy corresponding to the value of annual CUF declared in the PPA, on account of reasons solely attributable to the SPD, such shortfall in performance shall make the SPD liable to pay the compensation provided in the PPA (Power Purchase Agreement) to CoPA towards non-meeting of RPOs, if such compensation is ordered by the KSERC. The amount of compensation shall be equal to the compensation payable (including RECs ( Renewable Energy Certificate)) by the CoPA.

In case of shortfall in generation, the SPD shall provide necessary additional panels and arrangements for generating the required capacity as per the PPA. However, this compensation shall not be applicable in events of Force Majeure identified under the PPA, affecting supply of solar power by SPD.

### Excess Generation

While the SPD would be free to install DC solar field as per his design of required output, including his requirement of auxiliary consumption, he will not be allowed to sell any excess power to any other entity other than CoPA.

In case at any point of time, the peak of capacity reached is higher than the rated capacity and causes disturbance in the system at the point where power is injected, the SPD will have to forego the excess generation and reduce the output to the rated capacity to ensure compliance with grid requirement. In the case of excess power generation, use reverse power relay for avoiding export of solar energy into the grid. Hence reverse power relay is to be included in 11 kV VCB panel. While the SPD would be free to install DC solar field of his design of required output, as per the load data provided by CoPA, including his requirement of auxiliary consumption, he will not be allowed to sell any excess power to any other entity other than buying utility. The SPD shall arrange the Battery Energy Storage System (BESS) of sufficient capacity as per the load data provided by Port, for the storage of non-utilized power generated during low load conditions such as on holidays etc.

### CLEARANCES REQUIRED FROM THE STATE GOVERNMENT AND OTHER LOCALBODIES

  - The Solar Power Developers (SPDs) are required to obtain all the necessary approvals, grid connectivity approval from KSEBL, PPA approval from KSERC, clearances and permits including Environmental Clearance and Connectivity Approval, as required for setting up the Solar Power Projects. All the charges for obtaining such approvals, clearances and permits shall be borne by the SPD only.

The clearances, as applicable for the Project, shall be required to be submitted to CoPA prior to commissioning of the Project. In case of any of the clearances being not applicable for the said Project, the SPD shall submit an undertaking in this regard, and it shall be deemed that the SPD has obtained all the necessary approvals, clearances and permits for establishing and operating the Project. Any consequences contrary to the above hall be the responsibility of the SPD.

  - Any neglect or omission or failure on the part of the bidder in obtaining necessary clearances and reliable information upon the forgoing or any other matter affecting the bid shall not relieve him from any risks or liabilities or the entire responsibility for completion of the work in accordance with the bid.

#### CoPA shall arrange the connectivity procedures/ Protocol as per technical requirement issued by CEA from time to time. However SPD has to support and provide necessary materials, manpower and shall bear all the expenses in respect to get the connectivity.

- BID BOND/ EARNEST MONEY DEPOSIT(EMD)

  - All bids must be accompanied by a bid bond (EMD) of Rs.6,25,500/-. EMD shall be furnished in the form of Account Payee Demand Draft/ Banker’s Cheque/ Fixed Deposit Receipt /Bank Guarantee from a Commercial Bank in favour of “FA&CAO, Cochin Port Authority”, payable at Cochin or online payment in an acceptable form safeguarding the purchaser’s interest in all respects. The exemption shall be granted as per GFR 2017.

  - The Cost of tender document & EMD is exempted for MSME Vendors registered under NSIC/ UdyogAadhaar Category only. In order to avail the exemption in EMD in case of consortium/ JV, all the members should be registered as MSME Vendors under NSIC/ Udyog Aadhaar Categoryonly. The MSME certificate shall contain the item tendered, for exemption of EMD, otherwise they are not eligible for exemption of EMD.

- PERFORMANCE BANK GUARANTEE (Security Deposit)

  - Bidders selected by CoPA based on this RfS shall submit Performance Bank Guarantee for a value @ INR ---(as per contract value)--- within 21 days of issuance of Letter of Acceptance (LoA) or before signing of Provisional PPA, whichever is earlier. It may be noted that successful Bidders shall submit the Performance Bank Guarantee according to the Format 7.3 B for a value @ INR ----- with a validity period from the date of submission of the PBG until 18 (Eighteen) months from the Effective Date of the Provisional  PPA. On receipt and after successful verification of the total Performance Bank Guarantee in the acceptable form, the BG submitted towards EMD shall be returned by CoPA to the successful Bidder.  Non-submission of PBG within the above timelines shall be treated as follows:

- Delay upto 01 month from due date of submission of PBG: Delay charges @1% of the PBG amount per month levied on per day basis shall be paid by the Bidder to CoPA in addition to the PBG amount.

- Delay beyond 01 month from the due date of submission of PBG: The EMD submitted by the Bidder shall be en-cashed by CoPA and the Project shall stand terminated.

For the purpose of calculation of the above delay charges, ‘month’ shall be considered as a period of 30 days.

  - The Bidder shall furnish the PBG from any of the Banks listed at Schedule-2 of draft PPA to CoPA. PBG issued by foreign branch of a bank from banklist given in Schedule- 2 of draft PPA is to be endorsed by the Indian branch of the same bank or State Bank of India (SBI).

  - The format of the Bank Guarantees prescribed in the Formats 7.3 B (PBG) shall be strictly adhered to and any deviation from the above Formats shall result in rejection of the PBG and consequently, the bid. In case of deviations in the formats of the Bank Guarantees, the corresponding PPA shall not be signed.

  - The successful Bidders of the Projects selected based on this RfS are required to sign Provisional PPA with Cochin Port Authority (CoPA) with provision of separate Escrow account within 01 (One) month after the issuance of LOI. In case, CoPA offers to execute the Provisional PPA with the Selected Bidder and if the Selected Bidder does not submit the requisite documents as per Clause No. 14, Section-II, Instructions to Bidders (ITB) or does not meet eligibility criteria upon submission of documents or does not execute the PPA within the stipulated time period, then the Bank Guarantee equivalent to the amount of the EMD shall be forfeited by CoPA from theBank Guarantee available with CoPA (i.e.EMD or PBG) as liquidated damages not amounting to penalty, the selected Project(s) shall stand cancelled and the selected Bidder expressly waives off its rights and objections, if any, in that respect.

  - The Bank Guarantees have to be executed on non-judicial stamp paper of appropriate value as per Stamp Act relevant to the place of execution.

  - All expenditure towards execution of Bank Guarantees such as stamp duty etc. shall be borne by the Bidders.

  - In order to facilitate the Bidders to submit the Bank Guarantee as per the prescribed format and in line with the requirements, checklist at Annexure-B has been attached. Bidders are advised to take note of the above checklist while submitting the Bank Guarantees. After the bidding process is over, COPA shall release the Bank Guarantees towards EMD of the unsuccessful bidders within 30 days after the issuance of LOI to the successful bidder(s).The PBG of successful bidders/ developers/ SPDs shall be returned to them, immediately after successful commissioning of their projects as per Terms of PPA, after taking into account any liquidated damages due to delays in commissioning as per Clause No.16 ,Section-II, Instructions to Bidders (ITB) of RfS documents.

### PRE CONTRACT INTEGRITY PACT

The bidders have to execute an “Integrity Pact” (IP) as per the format available in CoPA’s website www.cochinport.gov.in., prepared in plain white paper. Integrity pact shall cover entire activities of this tender from bidding stage to the completion of defect liability period during various phases of this tender. The Tenderer should sign and submit the “Integrity Pact” to be executed between the Tenderer and Cochin Port Authority along with the Tender in a separate envelope super scribing “Integrity Pact”. Tenders not accompanied with IP will be rejected. The IP would be implemented through the following panel of Independent External Monitors (IEM) for this tender:

1) 	Shri. M J Joseph, ICAS (Rtd.)

37, Da Costa Square

3rd Cross, Cooke Town

Bangalore – 560 084

Email: joseph.iem@cochinport.gov.in

2) 	Shri. Punati Sridhar, IFoS( Retd)

8C, Block -4, 14-C Cross,

MCHS Colony, HSR 6th Sector,

Bangalore -560102

Email ID : sridhar.iem@ cochinport.gov.in

For full details of the scheme of IP, you may visit the website of Central Vigilance Commission, New Delhi.

### FORFEITURE OF EMD

The  EMD shall be forfeited by COPA in following cases:

(i) 	If the Bidder withdraws or varies the bid after due date and time of bid submission and during the validity ofbid;

(ii) 	In case, COPA offers to execute the PPA with the Selected Bidder and if the Selected Bidder does not submit the requisite documents as per Clause No. 14, Section-II, Instructions to Bidders (ITB) of RfS documents or does not execute the provisional PPA within the stipulated time period;

- If after issuance of LOI, it is found that the documents furnished by the Bidder as part of response to RfS are misleading or misrepresented in anyway;

- If the Bidder fails to furnish required Performance Bank Guarantee in accordance with Clause No. 11, Section-II, Instructions to Bidders(ITB) of RfS document.

### POWER PURCHASE AGREEMENT (PPA)

  - Cochin Port Authority (COPA) shall enter into Power Purchase Agreement (PPA) with Bidders with provision of separate Escrow account based on this RfS. A copy of standard Power Purchase Agreement (PPA) to be executed between COPA and the selected SPD will be made available on website of COPA https://www.cochinport.gov.in. The PPA shall be signed within 90 days from the date of issuance of LOI, or within 30 days from order date of KSERC in PPA.  (for e.g. If the LOI is dated 20.06.2022, PPA shall be executed between CoPA and selected bidder or its SPV, for the Project.

Note: Any changes in the location of the Project(s) awarded shall not be permitted. The PPAs shall be valid for a period of 25 years from the Scheduled Commissioning Date (SCD) of the Projects. However incase of any delay in commissioning of the project beyond 18 months from the effective date of LOI, the term of PPA shall be commenced w.e.f. end of 18thmonth onwards(Kindly refer clause no. 16.b for details).

  - The Performance Bank Guarantee as per Clasue 11 above, shall be submitted by the SPD prior to signing of LOA. Before signing of PPA with the selected Bidder, COPA will verify the documents furnished by the Bidder at the time of submission of response to RfS including the shareholding of the Project Company along with a copy of complete documentary evidence supported with the original documents. Bidders will be required to furnish the documentary evidence for meeting the RfS Qualification Requirement and financial requirements mentioned at Annexure to BDS respectively. At this stage, the Bidders shall be required to furnish the audited balance sheet of the previous month-end along with complete Bank Statement starting from day 1 of submission of response to RfS till date along with a copy of the documents submitted with ROC which became due during this period, along with all the relevant documents filed with MCA for allotment of Shares are required to be submitted at the time of signing of PPA. If at this stage it is found that the documents furnished by the Bidders are false/ misleading or misrepresented in any way then the provisions contained in this RfS will be applicable.

  - Power Sale Agreements (PSAs) are not applicable for this project.

The SPDs will be free to reconfigure and repower their plants from time to time during the PPA duration. However, CoPA will be obliged to buy power only within the Capacity Utilization Factor (CUF) range laid down in Power Purchase Agreement (PPA) as per guidelines. Also, the SPD shall arrange the Battery Energy Storage System (BESS) of sufficient capacity, if required as per the load data provided by Port, for the storage of non-utilized power generated during low/minimum load conditions such as on holidays etc. Any extension of the PPA period beyond 25 years shall be through mutual Agreement between the Solar Power Developer and CoPA subject to the approval of KSERC.

### FINANCIAL CLOSURE OR PROJECT FINANCING ARRANGEMENTS

  - The Project shall achieve Financial Closure within 06 (Six) months from the Effective Date of the Power Purchase Agreement (PPA) (for e.g. if Effective date of the PPA is 20.07.2022, then scheduled Financial Closure date shall be 20.01.2023). At this stage, the SPDs shall report tie-up of Financing Arrangements for the Projects. In this regard, the SPD shall submit a certificate from all financing agencies regarding the tie-up of funds indicated for the Project. Additionally, the SPD shall furnish documentary evidence towards the following:-

- The orders placed/agreements entered into, for supply of plants and equipment for the Project.

- Detailed Project Report for each Project.

- The details of all planned/ proposed Inverters and modules (manufacturer, model number, data sheet, all technical BIS / IEC certificates as mentioned at Annexure- A along with the link of the certifying authority with ILAC member accredited lab/NABL accredited lab) for the Project, at least 15(Fifteen) days prior to the scheduled Financial Closure date.

- Copies of all the clearances required for successful execution of the project.

  - In case of delay in achieving financial closure due to delay not attributable to the SPD, subsequent extension will begiven.

  - The SPD will have to submit the required documents to CoPA at least 15 (Fifteen) days prior to the scheduled Financial Closure date. In case of delay in submission of documents mentioned above, CoPA shall not be liable for delay in verification of documents and subsequent delay in Financial Closure.

  - In case the SPD submitted all the requisite documents to the concerned authority within 03 (Three) months from the date of execution of PPA and still awaits for clearance by the Statutory authority, then the delay in obtaining the concerned statutory clearance shall not be attributable to the SPD. The SPD need to submit an undertaking stating the reason for delay along with copy of application and the Financial Closure can be done pending that statutory document. However, the SPD needs to submit the pending statutory clearance document prior to commissioning of the project.

### COMMISSIONING

The Commissioning of the Projects shall be carried out by the SPDs in line with the procedure elaborated in draft PPA document (Commissioning Procedure at Annexure-A and Appendix-A-1 are for reference). CoPA may authorize any individual or committee or organization to witness and validate the commissioning procedure at site. Prior to the commissioning and on completion of the project, necessary approval for the solar plant from statutory body such as CEA/SLDC State electrical inspectorate etc shall be obtained by the SPD at its cost and risk. The Commissioning certificates shall be issued by CoPA after successful commissioning.

### PARTCOMMISSIONING

Part commissioning of the Project shall be accepted by CoPA subject to the condition that the minimum capacity for acceptance of first and subsequent part(s) commissioning shall be 0.5 MW, without prejudice to the imposition of penalty, in terms of the Provisional PPA on the part which is not commissioned. However, the SCD will not get altered due to part- commissioning. Irrespective of dates of part commissioning or full commissioning, the PPA will remain in force for a period of 25 (twenty-five) years from the SCD.

### COMMISSIONING SCHEDULE AND LIQUIDATED DAMAGE FOR DELAY IN COMMISSIONING

The Project shall be commissioned within 12 months from the date of signing of PPA. In this regard, a duly constituted committee will physically inspect and certify successful commissioning of the Project. In case of failure to achieve this milestone, provisions of PPA as mentioned below shall apply:-

    - Delay up to six months from the SCD: The total PBG amount shall be encashed on per day basis and proportionate to the balance capacity not commissioned. For example, in case of a Project of 50MWcapacity, if commissioning of 10 MW capacity is delayed by 18 days from the scheduled date, then the penalty shall be: PBG amount X (10/50) X(18/180).

    - The maximum time period allowed for commissioning of the full Project Capacity with encashment of Performance Bank Guarantee shall be limited to18 months from the Effective Date of the PPA. Incase, the Commissioning of the Project is delayed beyond 18 months from the Effective Date of the Provisional PPA, the PPA shall be inforce

### w.e.f. end of 18th month onwards without change in final closing period.

For the purpose of calculations for penalty, ‘month’ shall be considered consisting of 30 days.

| Illustration of Liquidated Damages (LD) Calculations: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Consider a SPD has be enselected for the implementation no fa Project of capacity of 150MW Total Performance Bank Guarantee Amount furnished by the SPD-Rs: 1000Lakh. - LD Conditions: - In case of delay upto 6 Months from SCD: Entire PBG amount (i.e. INR 3703.70/MW/Day) shall been cashed as Liquid ated Damages for the first six months of delay, calculated on per day basis and proportionate to the capacity not commissioned. - Consider that the Project commissioning (fo re.g.Project capacity150 MW) has been achieved in the following manner: |  |  |  |  |  |  |
|  | Sl. No. | Commissioned Capacity (MW) as on SCD | Capacity remaining Un-commissioned (MW) as on SCD | Date of Commissioning of the respective part | Delay from the Scheduled Commissioning date (days) |  |
|  | 1 | 100 | 50 | Scheduled Commissioning date | 0 |  |
|  | 2 | 50 | 0 | Scheduled Commissioning date + 150 Days | 150 |  |
| i) LD Calculation: In case of above commissioning schedule, for 100MW capacity commissioned within SCD (scenario 1) there will be no LD. For balance 50MW capacity (scenario 2), the LD calculation for encashment of PBG, shall be done as follows: Total LD: (50 MW X 150days X INR 3703.70/ MW/ Day) = INR 2,77,77,777/- Based on the above schedule, total LD payable by the SPD shall be INR 2,77,77,777/-. |  |  |  |  |  |  |

### EARLYCOMMISSIONING

The SPD shall be permitted for full commissioning as well as part commissioning of the Project even prior to the SCD. Incases of early part-commissioning, till the SCD, CoPA may purchase the generation @75% (Seventy Five Percent) of the PPA tariff at its sole discretion. However, in case the entire capacity is commissioned prior to the scheduled commissioning date, CoPA may purchase the generation at PPA Tariff approved by KSERC. Further, early part/ full commissioning of the Project and subsequent energy procurement from the same shall be subject to the approval of CoPA.

### Right to Contracted Capacity & Energy/ Penalty Clause for not achieving CUF

### The SPD will declare the CUF of the project and will be allowed to revise the same once within first year after COD of the project. Thereafter, the CUF for the Project shall remain unchanged for the entire term of the PPA. The declared annual CUF shall in no case be less than 21%. It shall be the responsibility of the SPD, entirely at its cost and expense to install such number of Solar panels and associate equipment (including arrangement of extra Reservoir/land for such installation) as may be necessary to achieve the required CUF, and for this purpose SPD shall make its own study and investigation of the Global Horizontal Irradiance (GHI) and other factors prevalent in the area which have implication on the quantum of generation. SPD shall maintain generation so as to achieve annual CUF within + 10% and -15% of the declared value till the end of 10 years from COD, subject to the annual CUF remaining minimum of 15%, and within +10% and -20% of the declared value of the annual CUF thereafter till the end of the PPA duration of 25 years. The annual CUF will be calculated every year from 1st April of the year to 31st March next year. The compensation due to shortfall in generation shall be applied to the amount of shortfall in generation during the Contract Year. The amount of compensation shall be equal to the compensation payable (including RECs) by CoPA towards non - meeting of RPOs, which shall ensure that the CoPA is offset for all potential costs associated with low generation and supply of power under the PPA, subject to a minimum of 25% (twenty-five per cent) of the cost of this shortfall in energy terms, calculated at PPA tariff. The amount being equal to the compensation payable by the CoPA for not meeting RPO is only a measure of damage. It shall not be construed that the compensation is payable by SPD only if the buying Entity are required to pay compensation for such not meeting of RPO or that the buying Entity or the SPD shall be required to prove or establish such payment of compensation for not meeting the RPO. SPD shall agree that the methodology specified herein above for calculation of liquidated damages payable by the SPD for shortfall in generation is a genuine and accurate pre-estimation of the actual loss that will be suffered by buying Entity. SPD shall further acknowledge that a breach of any of the obligations contained herein result in injuries and that the amount of the liquidated damages or the method of calculating the liquidated damages specified in this document is a genuine and reasonable pre-estimate of the damages that may be suffered by buying Entity in each case specified under this Agreement. However, this compensation shall not be applicable in events of Force Majeure identified under the PPA with COPA affecting supply of power by the SPD. Any excess generation over and above 10% of declared annual CUF may be purchased by CoPAat a fixed tariff of 75% (seventy-five percent) of the PPA tariff. However, the SPD shall inform at least 30 days in advance of such excess generation to CoPA, to enable CoPA to take necessary actions for the acceptance of this excess generated energy. CoPA shall be required to intimate its approval/refusal to the SPD, for buying such excess generation not later than 7 days of receiving the above offer from the SPD. While the SPD would be free to install DC solar field as per his design of required output, including his requirement of auxiliary consumption, he will not be allowed to sell any excess power to any other entity other than CoPA. In case at any point of time, the peak of capacity reached is higher than the rated capacity and causes disturbance in the system at the point where power is injected, the SPD will have to forego the excess generation and reduce the output to the rated capacity.

### COMMERCIAL OPERATION DATE(COD)

Commercial Operation Date (COD) shall be the date on which the commissioning certificate is issued upon successful commissioning of the full capacity of the Project or the last part capacity of the Project, as the case may be. The 25-year tenure of PPA shall be as per the provisions of PPA. The following milestone dates may therefore be observed and may fall on separate dates:

- Inter connection with Grid: This will be facilitated by the CoPA on the request of the SPD, and on submission of approval certificate from CEA and upon conducting harmonics tests successfully even if the project is only partially ready, to facilitate testing and allow flow of power generated into the grid to avoid wastage of Power.

- Commissioning of the Project: This will be on a date, when the project meets the criteria defined for project commissioning. CoPA may authorize any individual or committee or organization to declare the project commissioned onsite.

### MINIMUM PAID UP SHARE CAPITAL TO BE HELD BY PROJECT PROMOTER

  - The Bidder shall provide dedicated 11KV transmission line from the solar power plant location to 110KV s/s at W. Island, 3.5 KM away from solar plant including supply and laying of 11KV UG cables, supply and installation of necessary switchgears like 11KV VCB panel, relay protection system, SCADA facility, metering system etc to connect the solar plant at 11 KV grid of CoPA at 110KV S/s. Complete information in their  bid in reference to this RfS about the Promoters and upon issuance of Letter of Intent (LoI), the SPD shall indicate its shareholding in the company indicating the controlling share holding before signing of PPA with CoPA.

  - No change in the controlling share holding of the Bidding Company or Bidding Consortium shall be permitted from the date of submission of response to Rf Still the execution of the PPA. However, in case the Project is being set up by a listed Company, this condition will not be applicable.

  - Incase of SPVs: The successful Bidder, if  being a single  company, shall ensure that its share holding in the SPV/Project Company executing the PPA, shall not fall below 51% at any time prior to 01 (one) year from the COD, except with the prior approval of CoPA. In the event the successful bidder is a consortium, then the combined shareholding of the consortium members in the SPV/Project Company executing the PPA, shall not fall below 51% at any time  prior to 01 (one) year from COD, except with the prior approval of CoPA. However, in case the Project is being set up by a listed Company, this condition will not be applicable.

  - In case of the successful Bidder itself executing the PPA, it shall ensure that its promoters shall not cede Control (Control shall mean the ownership, directly or indirectly, of more than 50% of the voting shares of such Company or right to appoint majority Directors), till 01 (one) year from the COD, except with the prior approval of CoPA. However, in case the Project is being set up by a listed Company, this condition will not be applicable.

  - In case of companies having multiple promoters (but none of the share holders having more than 50% of voting rights and paid up share capital), it shall be considered as a company under joint control. In such cases, the share holding pattern in the company as submitted at the time of bidding, shall be maintained for a period of 01 (One) year after COD.

  - Any change in the share holding after the expiry of 01 year from COD can be undertaken under intimation to CoPA. Transfer of controlling share holding of the company developing the project within the same group of companies will however be allowed after COD with the permission of CoPA, subject to the condition that, the management control remains within the same group of companies.

  - In the event of Change in Shareholding/ Substitution of Promoters triggered by the Financial Institutions leading to signing of fresh PPA with a new entity, an amount of INR 10 Lakh per Transaction as Facilitation Fee (non-refundable) shall be remitted by the developer to COPA.

### STRUCTURING OF THE BID SELECTION PROCESS

  - Single stage, two cover bidding  has been envisaged under this RfS. Bidders have to submit both Techno-Commercial Bid and Financial Bid (Tariff) together in response to this RfS online. The preparation of bid proposal has to be in the   manner described in Clause No.23, Section-II, Instructions to Bidders (ITB) of RfS.

### INSTRUCTIONS TO BIDDERS FOR STRUCTURING OF BID PROPOSALS IN RESPONSE TO RfS

The bidder including its Parent, Affiliate or Ultimate Parent or any Group Company shall submit a single response to RfS.

Detailed Instructions to be followed by the bidders for online submission of response to RfS are stated at Annexure - D and Annexure - E

Submission of bid proposals by Bidders in response to RfS shall be in the manner described below:

- Covering Letter as per Format7.1.

- In case of a Bidding Consortium, a Power of Attorney in favour of the Lead Member issued by the other Members of the Consortium shall be provided in original as per format attached hereto as Format7.2.

In the event any Member of the Bidding Consortium (other than Lead Member) is a foreign entity, it may submit Board Resolutions in place of Power of Attorney for the purpose of fulfilling the requirements under this clause. Provided that such Board Resolutions shall be supported by an unqualified opinion issued by the legal counsel of such foreign entity stating that the Board Resolutions are incompliance with the applicable laws of the respective jurisdictions of the issuing Company and the authorizations granted therein are true and valid.

- Earnest Money Deposit (EMD) in DD Drawn in favour of FA&CAO, Cochin Port Authority or as per Clause 10 mentioned above.

- Board Resolutions, as per prescribed formats enclosed as per Format 7.4 duly certified by the Company Secretary or the Director of the relevant Bidder, as applicable to the Bidder and mentioned hereunder:

  - Board resolution from the Bidding Company or the Lead Member of the Consortium, as the case may be, in favour of the person signing the response to RfS and in the event of selection of the Projects and to sign the PPA with COPA. Additionally, Board Resolution from each of the Consortium Members in favour of the person signing Consortium Agreement shall also be submitted.

  - Board Resolution from the Bidding Company committing 100% (One Hundred Percent) of the equity requirement for the Project/Board Resolutions from each of the Consortium Members together in aggregate committing to 100% (One Hundred Percent) of equity requirement for the Project (in case of Bidding Consortium); and

  - Board Resolutions from each of the Consortium Members and Lead Member contributing such additional amount over and above the percentage limit (specified for the Lead Member and other member in the Consortium Agreement) to the extent becoming necessary towards the total equity share in the Project Company, obligatory on the part of the Consortium pursuant to the terms and conditions in the Consortium Agreement.

- In case of a Consortium, the Consortium Agreement between the Members in the Consortium asper Format 7.5 along with Board resolution from each Member of the Consortium for participating in Consortium.

- Format for Financial Requirements as per Format 7.6 along with the certificate from practicing Chartered Accountant/Statutory Auditors showing details of computation of the financial credentials of the Bidder.

- A disclosure statement as per Format 7.7 regarding participation of any related companies in the bidding process.

- Format for Technical Criteria as per Format 7.8 (to be filled out separately for each Project) in line with Clause No.15, Section-II, Instructions to Bidders (ITB) of RfS.

- Declaration by the Bidding Company/ Lead Member of Bidding Consortium for the Proposed Technology Tie Up as per Format 7.9 (to b filled out separately for each Project).

- Pre-contract Integrity Pact as per the format available at CoPA website, www.cochinport.gov.in, in plain white paper.

- Experience certificate substantiating the compliance of MQC regarding experience, duly certified by notary Public.

- Profile of the company, concurrent commitments etc

- Attachments

  - Memorandum of Association/Article of Association needs to be attached along with the bid. The Bidder should also highlight the relevant provision which identifies the objects relating to Power/Energy/Renewable Energy/Solar Power plant development.

    - In case, there is no mention of the above provisions in the MoA/ AoA of the bidding company, the same has to be amended and submitted prior to signing of Provisional PPA, if the Bidder is selected as Successful Bidder.

    - If the selected Bidder wishes to execute the project through a Special Purpose Vehicle (SPV), the MoA/ AoA of the SPV high lighting the relevant provision which highlights the objects relating to Power/Energy/Renewable Energy/Solar Power plant development has to be submitted prior to signing of Provisional PPA.

  - Certificate of Incorporation of Bidding Company/ all member companies of Bidding Consortium.

  - A certificate of shareholding of the bidding company, its Parent and Ultimate Parent (if any) duly certified by a practicing Chartered Accountant/ Company Secretary as on date within one week prior to the last date of bid submission, along with documents containing information about the promoters, and their share holding in the Bidder (as on a date within one week prior to the last date of bid submission) indicating the controlling share holding at the stage of submission of response to RfS as per Clause No.18, Section-II, Instructions to Bidders (ITB) of RfS. CoPA reserves the right to seek additional information relating to shareholding in promoter companies, their parents/ ultimate parents and other group companies to satisfy themselves that RfS conditions have been complied with and the Bidder will ensure submission of the same within the required time lines.

  - Certified copies of annual audited accounts for the last three financial years, i.e. FY 2018-19, 2019-20 and 2020-21.

### IMPORTANT NOTES AND INSTRUCTIONS TO BIDDERS

- Wherever information has been sought in specified formats, the Bidders shall fill in the details as per the prescribed format sand shall refrain from any deviations and referring to any other document for providing any information required in the prescribed format.

- The Bidders shall be shortlisted based on the declarations made by them in relevant schedules of RfS. The documents submitted online will be verified be fore signing of Provisional PPA in terms of ClauseNo.14, Section-II, Instructions to Bidders (ITB) of Rfs.

- If the Bidder/ Member in a Bidding Consortium conceal any material information or makes a wrong statement or misrepresents facts or makes a misleading statement in its response to RfS, in any manner what so ever, CoPA reserves the right to reject such response to RfS and/ or cancel the Letter of Award (LoA), if issued, and the Bank Guarantee provided up to that stage shall be encashed. Bidder shall be solely responsible for disqualification based on their declaration in the submission of response to RfS.

- If the event specified at 21.3 is discovered after the Effective Date of PPA, consequences specified in PPA shall apply.

- Response submitted by the Bidder shall become the property of the CoPA and CoPA shall have no obligation to return the same to the Bidder. However, the EMDs submitted by unsuccessful Bidders shall be returned as specified in Clause no. 11, Section-II, Instructions to Bidders (ITB) of RfS.

- All documents of the response to RfS (including RfS and subsequent Amendments/ Clarifications/Addenda, PPA and PSA) submitted online must be digitally signed by the person authorized by the Board as per Format7.4.

- The response to RfS shall be submitted as mentioned in Clause No. 20, Section-II, Instructions to Bidders (ITB) of RfS. No change or supplemental information to a response to RfS will be accepted after the scheduled date and time of submission of response to RfS. However, CoPA reserves the right to seek additional information from the Bidders, if found necessary, during the course of evaluation of the response to RfS.

- The bidder shall make sure that the correct, valid and operative Pass-Phrase to decrypt the relevant Bid-part is submitted in to the ‘Time Locked Electronic Key Box (EKB)’ after the deadline of Bid submission, and before the commencement of the Online Tender Opening Event (TOE) of Technical bid.

- All the information should be submitted in English language only. In case of foreign bidders having documents in other than English language, then the documents shall be translated in English language by certified translator and submitted.

- Bidders shall mention the name of the contact person and complete address and contact details of the Bidder in the covering letter.

- Response to RfS that are incomplete, which do not substantially meet the requirements prescribed in this RfS, will be liable for rejection by CoPA.

- Response to RfS not submitted in the specified formats will be liable for rejection by CoPA.

- Bidders delaying in submission of additional information or clarifications sought will be liable for rejection.

- Non-submission and/ or submission of incomplete data/ information required under the provisions of RfS shall not be construed as waiver on the part of CoPA of the obligation of the Bidder to furnish the said data/information unless the waiver is in writing.

- Only Court in Cochin shall have exclusive jurisdiction in all matters

### VALIDITY OF THE RESPONSE TO RfS

The Bidder shall submit the response to RfS which shall remain valid up to 240 (Two Hundred Forty) days from the last date of submission of response to RfS (“Bid Validity”). CoPA reserves the right to reject any response to RfS which does not meet the aforementioned validity requirement.

### BID PREPARATION COST

The Bidder shall be responsible for all the costs associated with the preparation of the response to RfS and participation in discussions and attending pre-bid meeting(s)etc. CoPA shall not be responsible in any way for such costs, regardless of the conduct or outcome of the bid process

### CLARIFICATIONS/ PRE-BID MEETING/ ENQUIRIES/AMENDMENTS

  - Clarifications/ Doubts, if any, on RfS document may be emailed and/ or submitted in person/  by post, addressed to the Chief Mechanical Engineer, CoPA on or before the Pre-bid meeting scheduled as per RfS..

  - CoPA will make effort to respond to the same in the Pre-Bid Meeting to be held as mentioned in the Bid Information Sheet. A compiled list of such questionnaire and CoPA’s response will be uploaded in the website https://gem.gov.in/, www.cochinport.gov.in&www.eprocure.gov.in .

No separate reply/ intimation will be given for the above, elsewhere.

  - APre-Bid Meeting shall be held as mentioned in the Bid Information Sheet (Link shall be provided to the firms requesting for the same).

  - Enquiries/ Clarifications may be sought by the Bidder from

| Name of the Authorized Person of COPA: | Contact Details: |
| --- | --- |
| Shri V. ThuraiPandian, Chief Mechanical Engineer, Cochin Port Authority, Cochin 9 | Phone (Off): 0484-2666639, 0484-2582300 E-mail: cme@cochinport.gov.in |
| Sri. Ajayakumar R.S. Executive Engineer (Ele) | Phone (Off): 0484-2582305 Email: ajayakumarrs@cochinport.gov.in |
| Shri. D.Ajith Kumar Executive Engineer (Ele), Project | Phone (Off): 0484-2582320, Email: ajithkumar@cochinport.gov.in |

### RIGHT OF CoPA TO REJECT ABID

CoPA reserves the right to reject any or all of the responses to RfS or cancel the RfS or annul the bidding process for any project at any stage without assigning any reasons whatsoever and without thereby any liability.

### POST AWARD COMPLIANCES

Timely completion of all the milestones i.e. signing of PPA, meeting Financial Closure Requirements/ Conditions Subsequent (PPA), Commissioning etc. will be the sole responsibility of SPD. CoPA shall not be liable for issuing any intimations/reminders to SPDs for timely completion of milestones and/or submission of compliance documents.

Any checklists hared with SPD by CoPA for compliance of above mentioned milestones to be considered for the purpose of facilitation only. Any additional documents required as per the conditions of Guidelines, RfS and PPA must be timely submitted by the SPD.

### OWNERSHIP OF THE PLANT AFTER 25YEARS

The Ownership of the installation including the water body shall be vested with Cochin Port Authority and SPD will be a lessee only during contract period and it shall be transferred to Cochin Port Authority after25years.

- APPLICABLE LAW

The Contract shall be interpreted in accordance with the laws of Cochin

- SETTLEMENT OF DISPUTE

31.1 If any dispute of any kind whatsoever arises between CoPA and Successful bidder in connection with or arising out of the contract including without prejudice to the generality of the foregoing, any question regarding the existence, validity or termination, the parties shall seek to resolve any such dispute or difference by mutual consent.

31.2	If the parties fail to resolve, such a dispute or difference by mutual consent, within 45 days of its arising, then the dispute shall be referred by either party by giving notice to the other party in writing of its intention to refer to arbitration as hereafter provided regarding matter under dispute. No arbitration proceedings will commence unless such notice is given.

31.3	In case the contractor is a public sector enterprise or a Government department:

31.3.1	In case the Contractor is a Public Sector Enterprise or a Government Department, the dispute shall be referred for resolution in Permanent Machinery for Arbitration (PMA) of the Department of Public Enterprise, Government of India. Such dispute or difference shall be referred by either party for Arbitration to the sole Arbitrator in the Department of Public Enterprises to be nominated by the Secretary to the Government of India in-charge of the Department of Public Enterprises. The award of the Arbitrator shall be binding upon the parties to the dispute, provided, however, any party aggrieved by such award may make a further reference for setting aside or revision of the award to the Law Secretary, Department of Legal Affairs, Ministry of Law & Justice, Government of India. Upon such reference the dispute shall be decided by the Law Secretary or the Special Secretary / Additional Secretary, when so authorized by the Law Secretary, whose decision shall bind the Parties finally and conclusive. The Parties to the dispute will share equally the cost of arbitration as intimated by the Arbitrator.

31.4 	In case the contractor is not a public sector enterprise or a Government department.

31.4.1 	In all other cases, any dispute submitted by a party to arbitration shall be heard by an arbitration panel composed of three arbitrators, in accordance with the provisions set forth below.

31.4.2 	CoPA and the Contractor shall each appoint one arbitrator, and these two arbitrators shall jointly appoint a third arbitrator, who shall chair the arbitration panel. If the two arbitrators do not succeed in appointing a third arbitrator within Thirty (30) days after the latter of the two arbitrators has been appointed, the third arbitrator shall, at the request of either party, be appointed by the Appointing Authority for third arbitrator which shall be the President, Institution of Engineers.

31.4.3 If one party fails to appoint its arbitrator within thirty (30) days after the other party has named its arbitrator, the party which has named an arbitrator may request the Appointing Authority to appoint the second arbitrator.

31.4.4 If for any reason an arbitrator is unable to perform its function, the mandate of the Arbitrator shall terminate in accordance with the provisions of applicable laws as mentioned in Clause 28 (Applicable Law) and a substitute shall be appointed in the same manner as the original arbitrator.

31.4.5 Arbitration proceedings shall be conducted with The Arbitration and Conciliation Act, 1996. The venue or arbitration shall be Cochin.

31.4.6 The decision of a majority of the arbitrators (or of the third arbitrator chairing the arbitration panel, if there is no such majority) shall be final and binding and shall be enforceable in any court of competent jurisdiction as decree of the court. The parties thereby waive any objections to or claims of immunity from such enforcement.

31.4.7 The arbitrator(s) shall give reasoned award.

31.5 	Notwithstanding any reference to the arbitration herein, the parties shall continue to perform their respective obligations under the agreement unless they otherwise agree.

31.6 	Cost of arbitration shall be equally shared between the Successful bidder or Contractor and CoPA

32 	FORCE MAJEURE

32.1 	Notwithstanding the provisions of clauses contained in this RFS document; the contractor shall not be liable to forfeit (a) Security deposit for delay and (b) termination of contract; if he is unable to fulfill his obligation under this contract due to force majeure conditions.

32.2 	For purpose of this clause, "Force Majeure" means an event beyond the control of the contractor and not involving the contractor's fault or negligence and not foreseeable, either in its sovereign or contractual capacity. Such events may include but are not restricted to Acts of God, wars or revolutions, fires, floods, epidemics, quarantine restrictions and fright embargoes etc. Whether a “Force majeure” situation exists or not, shall be decided by COPA and its decision shall be final and binding on the contractor and all other concerned.

32.3 	In the event that the contractor is not able to perform his obligations under this contract on account of force majeure, he will be relieved of his obligations during the force majeure period. In the event that such force majeure extends beyond six

33	OTHER CONDITIONS

33.1 	The Successful bidder shall not transfer, assign or sublet the work under this contract or any substantial part thereof to any other party without the prior consent of COPA in writing.

33.2 	The Successful bidder shall not display the photographs of the work and not take advantage through publicity of the work without written permission of CoPA and KWA.

33.3 	The Successful bidder shall not make any other use of any of the documents or information of this contract, except for the purposes of performing the contract.

33.4 	Successors and Assigns

In case CoPA or Successful bidder may undergo any merger or amalgamation or a scheme of arrangement or similar re-organization & this contract is assigned to any entity (ies) partly or wholly, the contract shall be binding mutatis mutandis upon the successor entities & shall continue to remain valid with respect to obligation of the successor entities.

33.5 	Severability:

It is stated that each paragraph, clause, sub-clause, schedule or annexure of this contract shall be deemed severable & in the event of the unenforceability of any paragraph, clause sub-clause, schedule or the remaining part of the paragraph, clause, sub-clause, schedule annexure & rest of the contract shall continue to be in full force & effect.

33.6	 Counterparts

This contract may be executed in one or more counterparts, each of which shall be deemed an original & all of which collectively shall be deemed one of the same instrument.

- Conditions for bid submission by JV

  - Companies/Contractors may jointly undertake contract/contracts. Each entity would be jointly and severely responsible for completing the task as per the contract, however declaration of the Lead member to be indicated by bidders, however JV has to designate in their MOU.  The firms with at least 26% equity holding each are allowed to jointly meet the legibility criteria.

  - Bid submitted by an unincorporated Joint Venture of companies (JV) /Consortium of companies (Consortium), shall comply with the following requirements:

  - There shall be a Joint Venture Agreement between the constituent firms specific for the contract package for which the bids are submitted. The JV Agreement shall include among other things, the joint venture’s objectives, the proposed management structures, the proposed distribution of responsibilities both financial as well as technical for execution of the work, the contribution of each partner to joint venture operation, the commitment of all partners to  jointly and severally liable for due performance, recourse/ sanctions within the joint venture in the event of default or withdrawal of any partner and arrangements for providing the required indemnities.

  - The most experienced partner will be nominated as the Lead Partner and his nomination shall be evidenced by submitting power of attorney signed by the legally authorized signatories of all the partners.

  - The Lead Partner of the joint venture will provide suitable experienced personnel for at least 3 (three) positions in the assignment during the whole period of contract execution and a statement to this effect should be included in the Joint Venture Agreement.

  - The bid and in the case of the successful bidder, the Agreement, shall be signed and / or executed in such a manner for making it legally binding on all partners (including operative parts of the ensuing Contract in respect of Agreement of Arbitration, etc.). The Contract shall be signed by legally authorized signatories of all partners.

  - The Lead Partner shall be authorized to incur liabilities and to receive instructions for and on behalf of the partners of the Joint venture and entire execution of the Contract including payment shall be carried out exclusively through the Lead Partner. A Statement to this effect should be included in the Joint Venture Agreement.

  - All partners of the Joint Venture shall be liable jointly and severally for the execution of the Contract in accordance with the Contract terms, and a Statement to this effect should be included in the Joint Venture Agreement.

  - Bid Security as required can be furnished by any partner but it shall be in the name of Joint venture.

  - Performance Guarantee, as required, will be furnished by all partner(s), out of their accounts, in proportion of their participation in joint venture.

  - Joint Venture Agreement shall contain a clause to the effect that there shall be a separate JV Bank Account (distinct from the Bank Account of the individual partners) to which the individual partners shall contribute their share capital and/or working capital.

  - Joint Venture Agreement shall also contain a clause to the effect that the financial obligation of the JV shall be discharged through the said JV Bank Account only and also all payment received by JV from the Employer shall be through that account only.

  - Participation by a firm in more than one JV /Consortium is not permissible. A firm who submits bid on individual capacity is not eligible to be a partner of a JV /Consortium.   In case a firm’s name appears in more than one bid then both application may be rejected.

  - Each partner must submit the complete documentation, or portions applicable thereto, required qualifying the firm for bidding.

  - All the partners of the JV/Consortium shall be jointly and severally liable for due performance, recourse/sanctions within the joint venture in the event of default of any partner and arrangements for providing the required indemnities.

  - Notwithstanding demarcation or allotment of work among the partners, each partner shall be liable for non performance of the whole contract irrespective of their demarcation or share of work.

  - The Lead Partner shall be authorized to act on behalf of the JV/Consortium.

  - All the correspondences between the Employer and the contractor shall be routed through the Lead Partner.

  - In the event of default by the Lead Partner, it shall be construed as default of the Contractor; and Employer will take action under relevant clause(s) of the Bid Document and/or General Terms and Conditions of Contract.

  - A legally binding Joint Venture/Consortium Agreement signed by authorized signatories of all the partners of the JV/Consortium, as per the proforma at Annexure-13 shall be enclosed with the bid.

  - In case, the Joint Venture/Consortium Agreement enclosed with the bid is not acceptable to the Employer, the JV /Consortium will modify the agreement so as to be acceptable to the Employer.

  - Power of attorney duly executed and signed by legally authorized signatories of all the partners, authorizing the Lead Partner (a) to submit bid, negotiate and conclude contract and incur all liabilities therewith on behalf of the partner(s) of the JV /Consortium during the bidding process; and (b) in the event of a successful bid, to incur liabilities and receive instructions for and on behalf of the partner(s) of the JV /Consortium and to carry out the entire execution of the contract including payment, exclusively through Lead Partner, as per the proforma at Annexure-14, which shall be duly authenticated by a notary public or equivalent certifying authority, shall be enclosed with the bid.

  - An undertaking that all the partners are jointly and severally liable to the Employer for the performance of the contract shall be enclosed with the bid.

  - In the event of any partner leaving the JV, it shall be intimated to the Employer within 30 days by other partner(s). Failure to do so shall be construed as default of the contractor and the Employer may take action under relevant clause(s) of the Bid Document and/or General Terms and Conditions of Contract

  - The contractor shall not alter its composition or legal status without the prior written permission of the Employer. Failure to do so shall be construed as default of the contractor and the Employer may take action under relevant clause(s) of the Bid Document and/or General Terms and Conditions of Contract.

  - Number of partners in JV/Consortium shall be limited to maximum of three.

  - Definition of the Technical Partner

The Technical Partner is the one who will collaborate with the other Partner / Partners to accomplish / share the technical knowhow and latest technology available in the market for the Site Survey, Design, Engineering, Manufacture and supply of PV Modules, Floating Panels, Anchoring / Mooring and other infrastructure required for the successful implementation of the project and shall honour  the commitment agreed upon in the Technical Partnership agreement  entered between them and Lead Partner and  shall not be liable for financial losses incurred by the other partner due to delay in execution of the project / statutory approvals and not liable for penal actions like Liquidated Damages and other aspects of the contract.

  - However if in the case of the Technical Partner wants to leave the project due to any disagreement between the Lead Partner and himself the Lead Partner shall bring it to the knowledge of the Cochin Port Authority and with prior written approval of the employer they can  engage a new Technical Partner.

# SIGNATURE OF BIDDER

# SECTION - III

QUALIFYING REQUIREMENTS FOR BIDDERS (QR)

Short listing of Bidders will be based on meeting the following Criteria:

### GENERAL ELIGIBILITYCRITERIA

- General

- The following categories of Bidders shall be eligible to participate in the Tender :

- Bidders meeting specified technical and Financial criteria and registered as Private Ltd. Company / Public Ltd. Company / Proprietary Firm.

- Bidders meeting specified Financial criteria registered as Private Ltd. Company / Public Ltd. Company / Proprietary Firm and meeting the specified Technical criteria through a competent technical partner registered as Private Ltd. Company / Public Ltd. Company / Proprietary Firm.

- Lead Partner representing through Joint venture / Consortium meeting the specified Financial Criteria registered as  Private Ltd. Company / Public Ltd. Company / Proprietary Firm and any member of Joint Venture / Consortium meeting the specified Technical Criteria registered as Private Ltd. Company / Public Ltd. Company / Proprietary Firm.

    - A copy of Certificate of Registration / Incorporation / Memorandum and Articles of Association, Partnership deed etc. as applicable shall be furnished in support of their claim.

    - In case of Bid submitted by JV/Consortium, the minimum eligibility criteria except financial turnover can be fulfilled collectively by the partners of the JV/ Consortium.

    - In the case of Bid submitted by JV/Consortium, the Lead partner of the JV shall meet the minimum eligibility criteria of financial turnover.

    - In the case of Bid submitted by the Bidder through Technical Partner, the Technical Partner shall meet the specified Technical Criteria.

- Technical Eligibility Criteria

The tenderers should have the experience of having successfully completed similar works during the last 7 (seven) years ending on the last date of the previous month in which the tender has been floated and should be either of the following:

- Three (3) similar completed works, each single contract costing not less than Rs.2,50,20,000/- (40% of estimated cost)  (or installed 0.60 MWp capacity plant) OR

- Two (2) similar completed works, each single contract costing not less that Rs.3,12,75,000/- (50% of estimated cost)  (or installed  0.75 MWp capacity plant)/- OR

- One (1) similar completed work costing not less than Rs. 5,00,40,000/- (80% of estimated cost)  (or installed  1.20MWp capacity plant)

Note:- (i) Similar works means “Site Survey, Design, Engineering, Manufacture, Supply, Storage, Civil work, Erection, Testing & Commissioning  of Solar Power Plants in a single contract or cumulative contracts”.

(ii) The list of projects commissioned during last 7 years ending 00/00/2022, indicating whether the project is grid connected, along with a copy of the Commissioning certificate and Work order/ Contract Agreement/ from the Client/Owner shall be submitted in support of the claim.

(iii) The estimate amount of Rs.6,25,50,000/- has been arrived from the Benchmark cost fixed by KSERC as per the revised Regulations (Renewable and Net metering)(first amendment) Regulations 2022. Since, as per Regulation there is no capacity range available above 500kW, we have considered the capacity range of 101-500kW, which is Rs.4.17Crore per MW, for calculation of estimate amount. The estimated cost of the project excludes the cost of BESS, cost of cables and other switch gears  required for connecting the Solar Plant to the 110 KV Sub Station located at Willingdon Island approximately at a distance of 3.5 KM from the project location.

- Financial Eligibility Criteria

  - Average Financial turnover of the tenderer during the last 3 financial years ending 31st March 2021, shall not be less than Rs.1,87,65,000/-. The bidder would be required to submit annual audited accounts for the last 3 financial years, up to FY 2021-22,   showing annual turnover from the Chartered Accountant. For meeting the above financial eligibility criteria, if the data is provided by the Bidder in USD, equivalent Indian Rupees of Net Worth and other financial parameters will be calculated by the Bidder using Reserve Bank of India’s reference rates prevailing on the date of closing of the accounts for the respective financial year. For currency other than USD, Bidders shall convert such currency into USD as per the exchange rates certified by their banker prevailing on the relevant date and used for such conversion.

- The Bid Bond (EMD) shall be remitted as per the Instruction to Bidders (ITB) of SBD.

- The Chief Mechanical Engineer of Cochin Port Authority reserves the right to reject/ cancel/ postpone /annul any one or all tenders at any stage of the tender, which will be binding on all bidders.

- All correspondence with regard to the above shall be to the following address. (By Post/e-mail/In Person)

  - Name of bid documentation issuance officer  : V. Thuraipandian

  - Designation of the officer: Chief Mechanical Engineer

  - Address: Office of the Chief Mechanical Engineer, 1st floor, Main administrative building, Cochin Port Authority, Cochin 682 009.

  - Telephone- 0091 484 2666639, 04842582300, 2582305, 2582320

  - Fax: 0091 484 2666639

  - E mail ID-  cme@cochinport.gov.in / ajayakumarrs@cochinport.gov.in /jayalakshmi@cochinport.gov.in / mini@cochinport.gov.in

# SECTION - IV

DEFINITIONS OF TERMS

  - "ACT" or "ELECTRICITYACT, 2003" shall mean the Electricity Act, 2003 and include any modifications, amendments and substitution from time to time;

  - “AFFILIATE” shall mean a Company that, directly or indirectly,

    - controls, or

    - is controlled by, or

    - is under common control with, a Company developing a Project or a Member in a Consortium developing the Project and control means ownership, directly or indirectly ,of more than 50% (fifty percent) of the voting shares of such Company or right to appoint majority Directors;

  - “APPROPRIATE COMMISSION” shall mean as defined in the PPA;

  - “BIDDER” shall mean Bidding Company (including a foreign company) or a Bidding Consortium submitting the Bid. Any reference to the Bidder includes Bidding Company/ Bidding Consortium, Member of a Bidding Consortium including its successors, executors and permitted assigns and Lead Member of the Bidding Consortium jointly and severally, as the context may require; foreign companies participating in the bidding process shall be registered as companies as per the rules of their country of origin;

  - “BIDDING CONSORTIUM” or “CONSORTIUM” shall refer to a group of Companies that have collectively submitted the response in accordance with the provisions of this RfS under a Consortium Agreement;

  - “BLOCK” shall mean a minimum capacity to be installed at a single location, which shall be not be less than 0.75 MW. The Blocks shall be configured in line with Clause 3 of Section-II (ITB) of the RfS;

  - “CAPACITYUTILIZATIONFACTOR(CUF)”shall have the same meaning as provided in CERC (Terms and Conditions for Tariff determination from Renewable Energy Sources) Regulations, 2009 as amended from time to time;

  - “CHARTERED ACCOUNTANT” shall mean a person practicing in India or a firm whereof all the partners practicing in India as a Chartered Accountant(s) within the meaning of the Chartered Accountants Act, 1949.

For Bidders incorporated in countries other than India, “Chartered Accountant” shall meanapersonorafirmpracticingintherespectivecountryanddesignated/registered under the corresponding Statutes/ laws of the respective country;

  - “COMPANY”shallmeanabodycorporateincorporatedinIndiaundertheCompanies Act, 1956 or the Companies Act, 2013, as applicable;

  - “COMMERCIALOPERATIONDATE(COD)”shall mean the date as defined in Clause no. 17, Section-II, Instructions to Bidders (ITB) of RfS;

  - “CONTRACTEDCAPACITY” shall mean the A Capacity in MW contracted with CoPA for supply by the SPD to CoPA at the Delivery Point from the Solar Power Project;

  - “CONTRACT YEAR” shall mean the period beginning from the Effective Date and ending on the immediately succeeding 31stMarch and thereafter each period of 12 months beginning on 1stApril and ending on 31stMarch provided that:

- in the financial year in which the Scheduled Commissioning Date would occur, the Contract Year shall end on the date immediately before the Scheduled Commissioning Date and a new Contract Year shall commence once again from the Scheduled Commissioning Date and end on the immediately succeeding 31st March, and thereafter each period of 12 (Twelve) Months commencing on1stApril and ending on 31st March, and

- provided further that the last Contract Year of this Agreement shall end on the last day of the Term of this Agreement;

  - “CONTROL” shall mean the ownership, directly or indirectly, of more than 50% (fifty percent) of the voting shares of such Company or right to appoint majority Directors;

  - “CONTROLLING SHAREHOLDING” shall mean more than 50% of the voting rights and paid up share capital in the Company/Consortium;

  - STATE TRANSMISSION UTILITY (STU)” shall mean the State  Transmission Utility, M/s Kerala State Electricity Board(KSEBL)

  - “DAY” shall mean calendar day;

  - “EFFECTIVE DATE” shall mean the date as on  from the date of issuance of Letter of Acceptance Intent (LOA), which shall be indicated in the Power Purchase Agreement (PPA) executed by both the parties;

  - “EQUITY” shall mean Net Worth as defined in Companies Act,2013;

“FINANCIAL CLOSURE” or “PROJECT FINANCING ARRANGEMENTS” means arrangement of necessary funds by the Solar Power Developer either by way of commitment of              funds by the Company from its internal resource and/or tie up of funds through a bank/ financial institution by way of sanction of a loan or letter agreeing to finance. For details kindly refer Clause no. 15, Section-II(ITB);

  - “FLOATING SOLAR” means a floating solar array or floating solar farm, refers to an array of photovoltaic panels on a structure that floats on a body of water, typically a reservoir or lake;

  - “LEAD MEMBER OF THE BIDDING CONSORTIUM” or “LEAD MEMBER”: There shall be only one Lead Member, having the share holding of not less 51%in the Bidding Consortium.

  - “GROUP COMPANY” of a Company means

- a Company which, directly or indirectly, holds 10% (Ten Percent) or more of the share capital of the Company or;

- aCompanyinwhichtheCompany,directlyorindirectly,holds10%(TenPercent)or more of the share capital of such Company or;

- a Company in which the Company, directly or indirectly, has the power to direct or cause to be directed the management and policies of such Company whether through the ownership of securities or agreement or any other arrangement or otherwise or;

- a Company which, directly or indirectly, has the power to direct or cause to be directed the management and policies of the Company whether through the ownership of securities or agreement or any other arrangement or otherwise or;

- a Company which is under common control with the Company, and control means ownership by one Company of at least 10% (Ten Percent) of the share capital of the other Company or power to direct or cause to be directed the management and policies of such Company whether through the ownership of securities or agreement or any other arrangement or otherwise;

Provided that a financial institution, scheduled bank, foreign institutional investor, Non- Banking Financial Company, and any mutual fund shall not be deemed to be Group Company, and its shareholding and the power to direct or cause to be directed the management and policies of a Company shall not be considered for the purposes of this definition unless it is the Project Company or a Member of the Consortium developing the Project;

  - “INTER-CONNECTION POINT/DELIVERY/METERING POINT” shall mean the point at 11kV at the 110KV substation, where the power from the Solar Power Projects is injected in to the identified termination point (including the dedicated transmission line connecting the solar power Projects with the substation systems such as UG cables, switch gears, metering panels etc) as specified in the RfS document. Metering shall be done at this interconnection point where the power is injected into. For interconnection with grid and metering, the SPDs shall abide by the relevant CERC/ SERC Regulations, SLDC rules, Grid Code, CEA Communication &  Cyber Security Regulations and Central Electricity Authority (Installation and Operation of Meters) Regulations, 2006 as amended and revised from time to time.

  - “JOINT CONTROL” shall mean a situation where a company has multiple promoters (but none of the shareholders has more than 50% of voting rights and paid up share capital);

Note: The share holding of the Lead member in the Project Company (Special Purpose Vehicle) cannot be changed till 01 (One) year after the Commercial Operation Date (COD) of the Project;

  - “LETTER OF AWARD” or “LoA” shall mean the letter issued by Cochin Port Authority(CoPA) to the selected Bidder for award of the Project;

  - “LIMITED LIABILITY PARTNERSHIP” or “LLP”shall mean a Company governed by Limited Liability Partnership Act 2008 or as amended;

  - “LLC” shall mean Limited Liability Company;

  - “MEMBER IN A BIDDING CONSORTIUM” or “MEMBER” shall mean each Company in a Bidding Consortium. In case of a Technology Partner being a member in the Consortium, it has to be a Company;

  - “MONTH” shall mean calendar month;

  - “NET-WORTH” means the Net-Worth as defined section 2 of the company Act,2013;

  - “PAID-UP SHARE CAPITAL” shall mean the paid-up share capital as defined in Section 2 of the Company Act,2013;

  - “PARENT” shall mean a Company, which holds not more than 50% voting rights and paid up share capital, either directly or indirectly in the Project Company or a Member in a Consortium developing the Project;

  - “PGCIL” means Power Grid Corporation of India Limited;

  - “PPA” shall mean the Power Purchase Agreement signed between the SPD and CoPA with provision of separate Escrow account according to the terms and conditions of the standard PPA enclosed with this RfS;

  - “PACKAGE” shall mean cumulative installation of 1.50 MW, to be interconnected at a single point. A Project may be divided into 02 Packages by the Bidder and shall be configured in line with Clause3 of Section-II (ITB) of the RfS;

  - “POWER PROJECT” or “FLOATING SOLAR POWER PROJECT” or “PROJECT” shall mean the solar power generation facility having separate points of injection into the grid at Inter-connection/Delivery/Metering Point, as illustrated in Clause no. 3 of Section II (ITB) of the RfS, a Project may comprise of 2 packages each of 0.75MWp with separate meters. However the injection point to the grid is a single point where power from 2 sources shall be synchronized to a single unit and connected to CoPA’s grid through a common grid meter and CT/PT units. The payment shall be made based on the energy shown in the common grid meter. The Project and/ or Package(s) shall include all units and auxiliaries such as water supply, treatment or storage facilities, bay(s) for transmission system in the switchyard, dedicated transmission lineup to the Delivery Point and all the other assets, buildings/structures, equipment, plant and machinery, facilities and related assets required for the efficient and economic operation of the power generation facility, whether completed or at any stage of development and construction or intended  to be developed and constructed or the purpose of supply of power to CoPA;

  - “PROJECT CAPACITY” shall mean the maximum A Capacity at the delivery point that can be scheduled on which the Power Purchase Agreement shall be signed;

  - “PROJECT COMMISSIONING”: The Project will be considered as commission edifall equipment as per rated project capacity has been installed and energy has flown into grid, inline with the Commissioning procedures defined in  the RfS/PPA;

  - “PROJECT DEVELOPER” or “DEVELOPER” or “SOLAR POWER DEVELOPER (SPD)” shall mean the Bidding Company or a Bidding Consortium participating in the bid and having been selected and allocated a project capacity by CoPA (through a competitive bidding process), including the SPV formed by the selected bidder/ consortium for the purpose of setting up of   project and signing of PPA with CoPA;

  - “RfS DOCUMENT” shall mean the bidding document issued by CoPA including all attachments, clarifications and amendments thereof vide RfSNo.F1/T-  / Floating solar-  /2022/M dt:00/00/2022.

  - “COPA” shall mean Cochin Port Authority;

  - “SELECTED BIDDER” or “SUCCESSFUL BIDDER” shall mean the Bidder selected pursuant to this RfS to set up the Project and supply electrical output as per the terms of PPA;

  - “SOLAR PV PROJECT” shall mean the Solar Photo Voltaic Power Project that uses sunlight for direct conversion into electricity through Photo Voltaic Technology;

  - “STATE TRANSMISSION UTILITY” or “STU” shall mean the Kerala State Electricity Board or the Government Company notified by the respective State Government under Sub-Section I of Section 39 of the Electricity Act,2003;

  - “TOE” shall mean Tender Opening Event.

  - “ULTIMATE PARENT” shall mean a Company, which owns more than 50% (Fifty Percent) voting rights and paid up share capital, either directly or indirectly in the Parent and Affiliates;

  - “KSEBL” shall mean Kerala State Electricity Board Limited;

  - “CERC” Means Central Electricity Regulatory Commission

  - “KSERC” Means Kerala State Electricity Regulatory Commission

  - “WEEK” shall mean calendar week;

# SECTION - V

BID EVALUATION AND SELECTION OF PROJECTS

### BIDEVALUATION

Bid evaluation will be carried out considering the information furnished by Bidders as per provisions specified in Section-II, Instructions to Bidders (ITB) of this RfS.

The evaluation process comprises the following four steps:

Step I - Responsiveness check of Techno Commercial Bid

Step II -Evaluation of Bidder’s fulfillment of Eligibility Criteria as per Clause 16

Step III -Evaluation of Price Bid and approval of the price/levllised tariff quoted by the successful bidder by the KSERC.

Step IV -Successful Bidders(s) selection

The detailed evaluation procedure and selection of bidders are described in subsequent clauses in this Section.

### TECHNO-COMMERCIAL EVALUATION OFBIDDERS

Each Bid shall be checked for compliance with the submission requirements set forth in this RfS before the evaluation of Bidder’s fulfillment of Eligibility Criteria is taken up.   During the examination of the bids, CoPA may seek clarifications/shortfall documents from the Bidders if required to satisfy themselves for meeting the eligibility conditions by the Bidders. Bidders shall be required to respond to any clarifications/ additional documents sought by CoPA within 07 (Seven) Days from the date of such intimation from CoPA. All correspondences in this regard shall be made through the mail only. The bidders shall send replies to the clarifications by mail attaching the documents as requested within the time given for replies.

Responsiveness check of Techno Commercial Bid

    - The Techno Commercial Bid submitted by Bidders shall be scrutinized to establish responsiveness to the requirements laid down in the RFS, Section III Eligibility Criteria. Any of the following may cause the Bid to be considered “Non-responsive”, at the sole discretion of CoPA.

- Bids that are incomplete, i.e. not accompanied by the Prequalification documents like Previous Work orders, Completion/Performance certificates and Financial Turn over certificates, Available bid capacity, Net worth and Profit etc.,

- Bid not signed by authorized signatory and /or stamped in the manner indicated in this RFS;

- Material inconsistencies in the information /documents submitted by the Bidder, affecting the Eligibility Criteria;

- Information not submitted in the formats specified in this RFS;

- Bid being conditional in nature;

- Bid having Conflict of Interest;

- More than one Member of a Bidding Company using the credentials of the same Parent Company /Affiliate;

- Bidder delaying in submission of additional information or clarifications sought by CoPA, as applicable;

- Bidder makes any misrepresentation.

Each Bid shall be checked for compliance with the submission requirements set forth in this RFS before the evaluation of Bidder’s fulfillment of Eligibility Criteria is taken up.

- Evaluation of Bidder’s fulfillment of eligibility criteria

Evaluation of Bidder’s Eligibility will be carried out based on the information furnished by the Bidder as per the prescribed Formats and related documentary evidence in support of meeting the Eligibility Criteria as specified in Section III Eligibility Criteria

- EVALUATION OF PRICE BID

The Price Bid of only the Qualified Bidders shall be opened in the GEM portal, on a date as may be intimated by CoPA to the Bidders through e-mail. The evaluation of Price Bid shall be carried out based on the information furnished in the BoQ. The Price bids shall be evaluated as follows:

  - The lowest tariff among the competitive bidders or tariff quoted by the Single qualified bidder per KWH, whichever is as per the tariff approved by the KSERC and contract will be awarded accordingly to the successful bidder.

  - In case KSERC approves / advises a revised tariff below the levelized tariff quoted by the lowest Bidder, then the lowest Bidder shall revise / reduce the tariff as per the KSERC directions, based on the written request of CoPA.

If in the case of the lowest Bidder not agreeing to the revised / reduced tariff as per the request of CoPA, the CoPA reserves the right to call for the reverse auction.

  - The CoPA reserves the right to conduct the Reverse auction among the Pre-qualified bidders whose financial bids have been opened in order to explore the possibility of determining the levelized tariff as per KSERC approval. The conduct of Reverse auction is at the sole discretion of the COPA.

### REVERSE AUCTION

  - The Reverse auction will be conducted at the discretion of Cochin Port Authority, among the bidders who have been pre qualified and the Financial Bids of those Bidders which have been opened.  The reverse auction will be conducted in the following situations.

      - In the case of lowest Bidder has quoted more than the tariff approved by the KSERC.

      - In the case of the lowest Bidder not agreeing to reduce the levelized tariff as per the approved tariff by the KSERC.

At least one week prior to reverse auction, an advance intimation regarding the date and time of the reverse auction will be informed to the Bidders among the Pre-qualified bidders whose financial bids have been opened.

    - During the 15 minutes prior to start of reverse auction process, the respective tariff of the Bidder shall be displayed on its window.

    - The minimum decrement value for tariff will be informed to the bidders while at the time of information of Reverse auction.

    - Bidders can only quote any value lower than their previous quoted tariff.

    - During reverse auction, the Bidder shall not have the option of changing the total Project capacity while quoting tariff during reverse auction

    - IntheBidder’sbiddingwindow,thefollowinginformationcanbeviewedbytheBidder:

      - Its tariff as the initial start price and there after last quoted tariff along with the Project capacity for which the Bidder is qualified.

      - The list of all the Bidders with their following details: Pseudo Identity, last quoted tariff and project capacity

- The initial auction period will be of 01 (One) Hour with a provision of auto extension by eight Minutes from the scheduled/ extended period will be allowed by the system, this extension of eight minutes will be automatically given till such time when there is no bids during the eight minutes period and after which the Reverse auction will be closed and no further bids will be accepted.

# SECTION - VI

OTHER PROVISIONS

### ROLE OF STATE NODAL AGENCIES

It is envisaged that the CoPA shall arrange project implementation team, with project coordinator who will provide necessary support to facilitate the required approvals and sanctions in a time bound manner so as to achieve commissioning of the Projects within the scheduled Time line. This may include facilitation in the               following areas:

  - Coordination among various State and Central agencies for speedy implementation of projects

  - Support during commissioning of projects and issue of commissioning certificates.

  - The cost involved for getting approvals, statutory clearance etc shall be borne by the SPD

### INTELLECTUAL PROPERTY/ COPYRIGHT AND PATENT

- The copyright in all drawings, documents and other materials containing data and information furnished to the Employer by the Contractor herein shall remain vested in the Contractor or, if they are furnished to the Employer directly or through the Contractor by any third party, including supplier so materials, the copy right in such materials shall remain vested in such third party. The Employer shall however be free to reproduce all drawings, documents, specification and other material furnished to the Employer for the purpose of the contract including, if required, for operation and maintenance of the facilities.

- The Contractor shall indemnify the Employer against third party claims of infringement of patent, trade mark or industrial design rights arising from use of goods or any part thereof in India.

- Any IPR related issue should be taken care by the SPD. COPA will not be responsible.

- The technology to be used for PV Modules, anchoring etc., shall be the latest in the market and got approved from the Engineer in charge of the Project.

# SECTION – VII

SAMPLE FORMS & FORMATS

FOR BID SUBMISSION

### FORMATS FOR BID SUBMISSION

The following formats are required to be submitted as part of the RfS. These formats are designed to demonstrate the Bidder’s compliance with the Qualification Requirements set forth in Section - III and other submission requirements specified in the RfS.

- Format of Covering Letter (Format7.1)

- Format for Power of Attorney (Format7.2)

- Details of past experience of contractors for similar works (Format 7.14)

- Details of proposed approach and methodology (Format 7.17)

- Technical Requirements for Grid Connected Solar PV Projects(Annexure-A)

- Integrity pact (Annexure F as per CoPA format available in the website)

Format 7.1

COVERING LETTER

### (The Covering Letters hould be submitted on the Letter Head of the    Bidding Company/Lead Member o f Consortium)

Ref.No.		Date:

From:	(Insert name and address of Bidding Company/Lead Member of Consortium)

Tel.#:

Fax#:

E-mail address#

To

The Chief Mechanical Engineer

Cochin Port Authority

Sub: Response to RfS No. ------------- for Selection of Solar Power Developers for Setting up of 1.5 MW Grid Connected Floating Solar Power Projects at Backwaters of Cochin Port Authority.

Dear Sir/ Madam,

We, the under signed…….[insertnameofthe‘Bidder’]havingread,examinedandunderstood in detail the RfS including Qualification Requirements in particular, terms and conditions of the standard PPA for supply  of power for 25 years to CoPA, here by submit our response to RfS.

We confirm that in response to the aforesaid RfS, neither we nor any of our Ultimate Parent Company/ Parent Company/ Affiliate/ Group Company has submitted response to RfS other than this response to RfS, directly or indirectly, in response to the aforesaid RfS (as mentioned in Format 7.7 under Disclosure). We also confirm that we including our Ultimate Parent Company/ Parent Company/ Affiliate/ Group Companies directly or indirectly have not submitted response to RfS for more than cumulative capacity of 1.5 MW, including this response to RfS.

We are submitting RfS for the development of following Solar PV Project(s): -

| Project No. | Capacity (MW) | Location of Project | Interconnection Point Details | Proposed CUF | Project Preference* |
| --- | --- | --- | --- | --- | --- |

*The preferences of the Projects shall be considered only for the last successful bidder whose total quoted capacity is more than the balance capacity. In this case, allocation will be done as described in Clause 4.3 of Section V of the RfS.

(Note: The Bidder must ensure the project capacity mentioned should be more than or equal to 0.75 MW and less than or equal to 1.5 MW for each project. Delete/Insert rows asapplicable)

- We give our unconditional acceptance to the RfS, dated	[Insert date in

dd/mm/yyyy], standard PPA documents attached there to,issuedbyCOPA.In token of our acceptance to the RfS, PPA documents along with the amendments and clarifications issued by COPA, the same have been digitally signed by us and enclosed with the response to RfS. We shall ensure that the PPA is executed as per the provisions of the RfS and provisions of PPA and shall be binding on us. Further, we confirm that the Project shall be commissioned within 12 months of the Effective Date of PPA.

- Earnest Money Deposit (EMD): - (Please read Section-II, ITB carefully before filling)

We have enclosed EMD of INR …………. (Insert Amount), in the form of Bank Guarantee no…………. [Insert bank guarantee number] dated ………. [Insert date of bank guarantee] as per Format 7.3A from	[Insert name of bank providing bank

guarantee] and valid upto	in terms of, Section-II, ITB of this RfS.

The total capacity of the Solar PV Project offered by us is …………. MW [Insert cumulative capacity proposed].

- We hereby declare that in the event our Project(s) get selected and we are not able to submit Bank Guarantee of the requisite value(s) towards PBG within due time as mentioned in, Section-II,ITB of this RfS on issue of LoI by CoPA for the selected Projects and/ or we are not able to sign PPA within the prescribed timelines with CoPA for the selected Projects, CoPA shall have the right to encash the EMD submitted by us and return the balance amount (if any)for the value of EMD pertaining to unsuccessful capacity.

- We have submitted our response to RfS strictly as per Section-VII (Sample Forms and Formats) of this RfS, without any deviations, conditions and without mentioning any assumptions or notes in the said Formats.

- We hereby declare that during the selection process, in the event our bid  happens to be the last bid in the list of successful bids and COPA offers a capacity which is less than our quoted capacity due to overall bid capacity limit, we shall accept such offered capacity.

- Acceptance:

We here by unconditionally and irrevocably agree and accept that the decision made by CoPA in respect of any matter regarding or arising out of the RfS shall be binding onus. We here by expressly waive and withdraw any deviation sandal claims in respect of this process.

- Familiarity with Relevant Indian Laws & Regulations:-

We confirm that we have studied the provisions of the relevant Indian Laws and Regulations as required to enable us to submit this response to RfS and execute the PPA, in the event of our selection as Successful Bidder.

- In case of our selection as the Successful bidder under the scheme and the project being executed by a Special Purpose Vehicle (SPV) incorporated by us which shall be our 100% subsidiary, we shall infuse necessary equity to the requirements of RfS. Further we will submit a Board Resolution prior to signing of PPA with CoPA, committing total equity infusion in the SPV as per the provisions of RfS.

- We hereby undertake that in the event of four project being selected under the RfS, we shall be solely responsible for getting the connectivity prior to commissioning of the Project. In the event of delay in commissioning with the grid of CTU beyond 06 months, the provisions of the RfS/ relevant articles of PPA shall be applied on such projects. Further, the project shall not be considered as commissioned unless the connectivity with CTU grid is established.

- We are submitting our response to the RfS with formats duly signed as   desired by you in the RfS online for your consideration.

- It is confirmed that our response to the RfS is consistent with all the requirements of submission as stated in the RfS, including all clarifications and amendments and subsequent communications from COPA.

- The information submitted in our response to the RfS is correct to the best of our knowledge and understanding. We would be solely responsible for any errors or omissions in our response to the RfS.

- We confirm that all the terms and conditions of our Bid are valid upto   -----------(Insert date in dd/mm/yyyy) for acceptance [i.e. a period of 240 (Two Hundred Forty) Days from the last date of submission of response to RfS].

- Contact Person

Details of the representative to be                                                                                                                                              contacted by COPA are furnished as under: Name	:	……………………………………

Designation	:	……………………………………

Company	:	……………………………………

Address	:	……………………………………

Phone Nos.	:	……………………………………

Mobile Nos.	:	……………………………………

FaxNos.	:	……………………………………

E-mail address	:	……………………………………

- We haveneithermadeanystatementnorprovidedanyinformationinthisBid,whichto the best of our knowledge is materially inaccurate or misleading. Further, all the confirmations, declarations and representations made in our Bidaretrue and accurate. In case this is found to bein correct after our selection as Successful Bidder, we agree that the same would be treated asa Seller’ sevent of default under PPA and consequent provisions of PPA shall apply.

Dated the	day of	, 20…. Thanking you,

We remain,

Yours faithfully,

Name, Designation, Seal and Signature of Authorized Person in whose name Power of Attorney/ Board Resolution/ Declaration.

Format 7.2

PROFORMA OF POWER- OF-ATTORNEY/LETTER OF AUTHORITY

(To be submitted on Non-judicial Stamp Paper of appropriate value)

To

The Chief Mechanical Engineer,

Cochin Port Authority,

Cochin 682009.

Kerala, India.

Dear Sir,

We____________________________________________________________________

do here by confirm that Mr./Ms./Messrs____________________________ [INSERT NAME AND ADDRESS], whose signature is given below, is /are authorized to represent us to bid, negotiate and conclude the agreement on our behalf with you against Tender for  “----------------------”

(Tender No…………..).

We confirm that we shall be bound by all and whatsoever our said agents shall commit.

Signature of the authorized person  :

Name & Designation	:

Yours faithfully,

Signature, name and seal of the certifying authority

FORMAT FOR POWER OF ATTORNEY

### (Applicable Only incase of Consortiums)

(TobeprovidedbyeachoftheothermembersoftheConsortiuminfavoroftheLeadMember)

(To be stamped in accordance with Stamp Act, the Non-Judicial Stamp Paper of Appropriate Value)

KNOW ALL MEN BY THESE PRESENTS THAT M/s…………….……………. having its registered office at ………………………….……., ….,and M/s	having its

registered office at …………………………………., (Insert names and registered offices of all Members of the Consortium) the Members of Consortium have formed a Bidding Consortium named ……………………. (insert name of the Consortium if finalized) (hereinafter called the ‘Consortium’) vide Consortium Agreement dated……….……………… and having agreed to appoint M/s	as the Lead Member of the said Consortium do hereby

constitute, nominate and appoint M/s	a company incorporated under the

laws of ……….………and having its Registered/ Head Office at	as

our duly constituted lawful Attorney (herein after called as Lead Member) to exercise all or any of the powers for and on behalf of the Consortium in regard to submission of the response to RfS No……………..

We also authorize the said Lead Member to undertake the following acts:

  - To submit on behalf of Consortium Members response to RfS.

  - To do any other act or submit any information and document related to the above response to RfS Bid.

It is expressly understood that in the event of the Consortium being selected as Successful Bidder, this Power of Attorney shall remain valid, binding and irrevocable until the Bidding Consortium achieves execution of PPA.

We as the Member of the Consortium agree and under take to ratify and confirm all whatsoever the said Attorney/ Lead Member has done on behalf of the Consortium Members pursuant to this Power of Attorney and the same shall bind us and deemed to have been done by us.

IN WITNESS WHERE OFM/s	, as the Member of the

Consortium have executed these presents on this………. day of under the Common Seal

of our company.

For and on behalf of Consortium Member

M/s………………………….

--------------------------------(Signature of person authorized by the board) (Name

Designation Place: Date:)

Accepted

(Signature, Name, Designation and Address

of the person authorized by the board of the Lead Member)

Attested

(Signature of the executants)

(Signature & stamp of Notary of the place of execution)

Place:

Date:

Lead Member in the Consortium shall have the controlling  share holding  in  the Company as defined in Section-IV, Definition of Terms of the RfS.

Format 7.3A

FORMAT FOR EARNEST MONEY DEPOSIT (EMD)

(To be stamped in accordance with Stamp Act, the Non-Judicial Stamp Paper of Appropriate Value)

Reference:  ……………………………….

Bank GuaranteeNo.:........................…

Date: ...................……...

In consideration of the ----- [Insert name of the Bidder] (hereinafter referred to as 'Bidder') submitting the response to RfS interalia for selection of the Project/Projects of the cumulative capacity of   -------MW [Insert cumulative Project capacity proposed] for supply of power there from on long term basis, in response to the RfS No.	dated	issued by Cochin Port Authority (hereinafter referred to as CoPA) and CoPA considering such response to the RfS  of	[insert the     name of the Bidder] as per the terms of   the RfS, the	[insert   name  &  address  of   bank]   hereby agrees unequivocally, irrevocably and un conditionally to pay to CoPA at [Insert Name of the Place from the address of CoPA] forth with on demand in writing from CoPA or any Officer authorized by it in this behalf, any amount up to and not exceeding Rupees	[Insert amount not less than that derived on the basis of 1 to 5% of the estimate value]__only, on behalf of M/s	[Insert name of the Bidder].

This guarantee shall be valid and binding on this Bank upto and including  -------------[insert date of validity in accordance with Clause No.--, Section-II, ITB of this RfS] and shall not be terminable by notice or any change in the constitution of the Bank or the term of contractor by any other reasons whatsoever and our liability hereunder shall not be impaired or discharged by any extension of time or variations oralternations made, given, or agreed with or without our knowledge or consent, by or between parties to the respective agreement.

Our   liability  under   this   Guarantee  is  restricted to INR	(Indian Rupees

only).    Our    Guarantee    shall    remain    in    force   until 	[insert date of validity in accordance with Clause No. --, Section-II, ITB of this RfS]. CoPA shall be entitled to invoke this Guarantee till	[insert date of validity in accordance with Clause No. --, Section-II, ITB of thisRfS].

The Guarantor Bank hereby agrees and acknowledges that the CoPA shall have a right to invoke this BANK GUARANTEE in part or in full, as it may deem fit.

The Guarantor Bank hereby expressly agrees that it shall not require any proof in addition to the written demand  by CoPA, made in any format, raised at the above mentioned address of the Guarantor Bank, in order to make the said payment to CoPA.

The Guarantor Bank shall make payment hereunder on first demand without restriction or condition sand not withstanding any objection by [Insert name of the Bidder] and/or any other person. The Guarantor or Bank shall not require CoPA to justify the invocation of this BANK GUARANTEE, nor shall the Guarantor Bank have any recourse against CoPA in respect of any payment made here under.

This BANK GUARANTEE shall be interpreted in accordance with the laws of India and the courts at New Delhi shall have exclusive jurisdiction.

The Guarantor Bank represents that this BANK GUARANTEE has been established in such form and with such content that it is fully enforceable in accordance with its terms as against the Guarantor Bank in the manner provided herein.

This BANK GUARANTEE shall not be affected in any manner by reason of merger, amalgamation, restructuring or any other change in the constitution of the Guarantor Bank.

This BANK GUARANTEE shall be a primary obligation of the Guarantor or Bank and accordingly CoPA shall not be obliged before enforcing this BANK GUARANTEE to take any action in any court or arbitral proceedings against the Bidder, to make any claim against or any demand on the Bidder or to give any notice to the Bidder or to enforce any security held by CoPA or to exercise, levy or enforce any distress, diligence or other process against the Bidder.

The Guarantor Bank acknowledges that this BANK GUARANTEE is not personal to CoPA and may be assigned, in whole or in part,(whether absolutely or by way of security)by CoPA to any entity to whom CoPA is entitled to assign it srights and obligations under the PPA.

Notwithstanding any thing contained here in above, our liability under this Guarantee is restricted to INR	--------(Indian Rupees	Only)and it shall remain in force until		[Date to be inserted on the basis of Clause No. --, Section-II, ITB of this RfS].

We are liable to pay the guaranteed amount or any part thereof under this Bank Guarantee only if CoPA serves upon us a written claim or demand.

Signature:

Name:

Power of Attorney No.:

For

[Insert Name and Address of the Bank]

Contact Details of the Bank: E-mail ID of the Bank:

Banker's Stamp and Full Address. Dated this	day of _	,20

Format 7.3B

PROFORMA OF IRREVOCABLE BANK GUARANTEE FOR PERFORMANCE GUARANTEE

(To be on non-judicial stamp paper of appropriate value as per Stamp Act relevant to Kerala)

In consideration of the ----- [Insert name of the Bidder] (hereinafter referred to as selected Successful Bidder(SB)) submitting the response to RfS    for the capacity of ……….. MW under Floating solar PV Project in response to the RfS No	_ dated………… issued by Cochin Port Authority (hereinafter  referred to as CoPA) and COPA considering such response to the RfS of ………[insert the name of the Successful Bidder] (which expression shall unless repugnant to the context or meaning thereof include its executers, administrators, successors and assignees) and selecting the Solar Power Project of the Solar Power Developer and issuing Letter of allocation No ------------- to------------(insert the name of the Successful Bidder(SB)) as per terms of RfS and the same having been accepted by the selected SB or a Project Company, M/s ------------- {a Special Purpose Vehicle  (SPV)  formed for this purpose}, ifapplicable ].As per the terms of the RfS,the		[insert name & address of bank] hereby agrees unequivocally, irrevocably and unconditionally to pay to COPA at_	[Insert Name of the Place from the address] of the COPA forthwith on demand in  writing  from COPA or any Officer authorised by it in this behalf, any amount upto and not exceeding Rupees		[Total  Value]  only,   on   behalfof M/s	Bidder(SB)/ Project Company] [Insert name of the selectedSuccessful bidder

This guarantee shall be valid and binding on this Bank up to and including……….[insert  date of validity]. and shall not be terminable by notice or any change in the constitution of the Bank or the term of contract or by any other reasons whatsoever and our liability hereunder shall not  be  impaired  or  discharged  by any extension of time or  variations  or alternations made, given, or agreed with or without our knowledge or consent, by or between parties to the respectiveagreement.

Our   liability   under   this   Guarantee   is   restricted  to  Rs.		(Rs.	only) Our  Guarantee  shall  remain  inforceuntil	[insert date of validity) COPA shall be entitled to invoke this Guarantee till [Insert  date which is  30 days after  the date in the preceding   sentence].

The Guarantor Bank hereby expressly agrees that it shall not require any proof in addition to the written demand Cochin Port Authority, made in any format, raised at the above mentioned address of the Guarantor Bank, in order to make the said payment to Cochin Port Authority.

The Guarantor  Bank  shall  make  payment  hereunder  on  first  demand  without  restriction or conditions and notwithstanding any objection by -------------[Insert name of the Successful Bidder(SB)/ Project Company as applicable] and/or any other person. The Guarantor Bank shall not require COPA to justify the invocation of this BANKGUARANTEE,nor shall the Guarantor Bank have any recourse against COPA in respect of any payment made hereunder.

This BANK GUARANTEE shall be interpreted in accordance with the laws of India and the courts at Ernakulam  shall have exclusive jurisdiction.

The Guarantor Bank represents that this BANK GUARANTEE has been established in such form and with such content that it is fully enforceable in accordance with its terms as against the Guarantor Bank in the manner provided herein.

This BANK GUARANTEE shall not be affected in any manner by reason of merger, amalgamation, restructuring or any other change in the constitution of the Guarantor Bank.

This BANK GUARANTEE shall be a primary obligation of the Guarantor Bank and accordingly COPAshall not be obliged before enforcing this BANK GUARANTEE to take any action in any court or arbitral  proceedings  against  the Successful Bidder(SB) / Project Company , to make any claim against or any demand on the Successful Bidder(SB)/ Project Company or to give any notice to the  Successful  Bidder(SB)/ Project Company or to  enforce  any  security  held  by  COPA or to exercise, levy or enforce any distress, diligence or other process against the Successful Bidder(SB)/ Project Company.

Notwithstanding anything contained hereinabove, our liability under this Guarantee is restricted to Rs. (Rs.	_only)and it shall remainin forceuntil …………….. We are liable to pay the guaranteed amount or any part thereof under this Bank Guarantee only if COPA serves upon us a written claim or demand.

Signature_	_

Name

Power of Attorney No.

Email ID

For

[Insert Name oftheBank]	 Banker's Stamp and Full Address. Dated this day of___	, 20__

Witness:

1.……………………..……. Signature

Name

Address

- ………………………... Signature Name and Address

Format 7.4

FORMAT FOR BOARD RESOLUTIONS

The Board, after discussion, at the duly convened Meeting on	[Insert date], with the

Consent of all the Directors present and incompliance of the provisions of the Companies Act, 1956 or Companies Act2013,as applicable, passed the following Resolution:

- RESOLVED THATMr/Ms	, be and is hereby authorized to do on our behalf,

all such acts, deeds and things necessary in connection with or incidental to our response to RfS vide RfS No.	for 'Selection of 1.5 MW(50MW x 03) Grid Connected Floating Solar Power Projects' in Backwaters of Cochin Port Authority, India, including signing and submission of all documents and providing information/ response to RfS to Solar Energy Corporation of India Limited(COPA),representing us in all matters before COPA, and generally dealing with COPA in all matters in connection with our bid for the said Project. (To be provided by the Bidding Company or the Lead Member of the Consortium)

- FURTHER RESOLVED THAT pursuant to the provisions of the Companies Act, 1956 or Companies Act, 2013, as applicable and compliance thereof and as permitted under the Memorandum and Articles of Association of the Company, approval of the Board be and is hereby accorded to invest total equity in the Project. (To be provided by the Bidding Company)

#### [Note:In the event the Bidder is a Bidding Consortium, in place of the above resolution at Sl. No. 2, the following resolutions are to beprovided]

FURTHER RESOLVED THAT pursuant to the provisions of the Companies Act, 1956 or Companies Act, 2013, as applicable and compliance thereof and as permitted under the Memorandum and Articles of Association of the Company, approval of the Board be and is hereby accorded to invest (-----%) equity [Insert the % equity commitment as specified in Consortium Agreement] in the Project. (To be provided by each Member of the Bidding Consortium including Lead Member such that total equity is 100%)

FURTHER RESOLVED THAT approval of the Board beandishere by accorded to participate in consortium with M/s	[Insert the name of other Members in the Consortium] and Mr/

Ms	, be and is hereby authorized to execute the Consortium Agreement. (To be

#### provided by each Member of the Bidding Consortium including Lead Member)

And

FURTHER RESOLVED THAT approval of the Board be and is hereby accorded to contribute such additional amount over and above the percentage limit (specified for the Lead Member in the Consortium Agreement) to the extent becoming necessary towards the total equity share in the Project Company, obligatory on the part of the Consortium pursuant to the terms and conditions contained in the Consortium Agreement dated	executed

by the Consortium as per the provisions of the RfS. [To be passed by the Lead Member of the Bidding Consortium]

### NOTUSED

Certified TrueCopy

----------------------------

(Signature, Name and Stamp of Company Secretary) Notes:

  - This certified true copy should be submitted on the letterhead of the Company, signed by the Company Secretary/Director.

  - Thecontentsoftheformatmaybesuitablyre-wordedindicatingtheidentityoftheentity passing the resolution.

  - Thisformatmaybemodifiedonlytothelimitedextentrequiredtocomplywiththelocal regulations and laws applicable to a foreign entity submitting this resolution. For example, eference to Companies Act, 1956 or Companies Act, 2013 as applicable may be suitably modified to refer to the law applicable to the entity submitting there solution. However, in such case, the foreign entity shall submit an unqualified opinion issued by the legal counsel of such foreign entity, stating that the Board resolutions are in compliance with the applicable laws of the respective jurisdictions of the issuing Company and the authorizations granted therein are true and valid.

### Certified True Copy

----------------------------

(Signature, Name and Stamp of Company Secretary) Notes:

- This certified true copy should be submitted on the letterhead of the Company, signed by the Company Secretary/Director.

- The content soft he format may be suitablyre-word edindicating the identity of the entity passing the resolution.

- This format may be modified only to the limited extent required to comply  with the local regulations and laws applicable to a foreign entity submitting this resolution. For example, reference to Companies Act, 1956 or Companies Act ,2013 as applicable may be suitably modified to refer to the law applicable otheentity submitting there solution. However, in such case, the foreign entity shall submit an unqualified opinion issued by the legal counsel of such foreign entity, stating that the Board resolutions are in compliance with the applicable laws of the respective jurisdictions of the issuing Company and the authorizations granted therein are true and valid

Format 7.5

FORMAT FOR CONSORTIUM AGREEMENT

(TobestampedinaccordancewithStampAct,theNon-JudicialStampPaperofAppropriate Value)

THIS Consortium Agreement (“Agreement”) executed on this Day of	Two Thousand	between M/s		[Insert name of Lead Member ]a Company incorporated under the laws of	and having its Registered Office

at	(hereinafter   called   the   “Member-1”, which

expression  shall  include  its  successors,   executors    and   permitted    assigns)   andM/s

a  Company  incorporated  under  the  laws  of

and  having  its  Registered Office at			(hereinafter called the “Member-2”, which expression shall  include  its  successors, executors    and    permitted  assigns),M/s		a Company  incorporated  under  the laws of	and having its Registered Office at

(herein after called the “Member-n”, which expression shall include  its  successors, executors and permitted assigns), [The Bidding Consortium should list the details of all the Consortium Members] for the purpose of submitting response to RfS and execution of Power Purchase Agreement  (in case of award), against RfSNo.	dated	issued by Cochin Port Authority (COPA) a Company incorporated under the Companies Act, 2013, and having its Registered Office at D-3, 1stFloor, Wing-A, Prius Platinum Building, District Centre, Saket, NewDelhi-110017

WHEREAS, each Member individually shall be referred to as the “Member” and all of the Members shall be collectively referred to as the “Members” in this Agreement.

WHEREAS COPA desires to purchase Power under the said RfS.

WHEREAS, COPA had invited response to RfS vide its Request for Selection (RfS) No.F2/T-13/ Floating Solar-1.5MWp-RT/2020/M Dated 08/09/2020

WHEREAS the RfS stipulates that in case response to RfS is being submitted by a Bidding Consortium, the Members of the Consortium will have to submit a legally enforceable Consortium Agreement in a format specified by COPA wherein the Consortium Members have to commit equity investment of a specific percentage for the Project.

NOW THEREFORE, THIS AGREEMENT WITNESSTH AS UNDER:

In consideration of the above premises and agreements all the Members in this Bidding Consortium do hereby mutually agree as follows:

- We, the Members of the Consortium and Members to the Agreement do hereby unequivocally  agree  thatMember-1(M/s	), shall act as the Lead Member as defined in the RfS for self and agent for and on behalf ofMember-2, --------, Member-n and to submit the response to the RfS.

- The Lead Member is hereby authorized by the Members of the Consortium and Members to the Agreement to bind the Consortium and receive instructions for and on their behalf.

- Not with standing any thing contrary contained in this Agreement, the Lead Member shall always be liable for the equity investment obligations of all the Consortium Members i.e. for both its own liability as well as the liability of other Members.

- The Lead Member shall be liable and responsible for ensuring the individual and collective commitment of each of the Members of the Consortium in discharging all of their respective equity obligations. Each Member further undertakes to be individually liable for the performance of its part of the obligations without in any way limiting the scope of collective liability envisaged in this Agreement.

- Subject to the term so this Agreement, the share of each Member of the Consortium in the issued equity share capital of the Project Company is/shall be in the following proportion:

| Name | Percentage |
| --- | --- |
| Member 1 | --- |
| Member 2 | --- |
| Member n | --- |
| Total | 100% |

We acknowledge that after the execution of PPA, the controlling shareholding (having not less than 51% of the voting right sand paid-up share capital) in the Project Company developing the Project shall be maintained for a period of 01 (One) Year after commencement of supply of power.

- The Lead Member, on behalf of the Consortium, shall inter alia undertake full responsibility for liaising with Lenders or through internal accruals and mobilizing debt resources for the Project, and ensuring that the Seller achieves Financial Closure in terms of the PPA.

- In case of any breach of any equity investment commitment by any of the Consortium Members, the Lead Member shall be liable for the consequences thereof.

- Except as specified in the Agreement, it is agreed that sharing of responsibilities as aforesaid and equity investment obligations thereto shall not in any way be a limitation of responsibility of the Lead Member under these  presents.

- It is further specifically agreed that the financial liability for equity contribution of the Lead Member shall not be limited in any way so as to restrict or limit its liabilities. The Lead Member shall  be liable irrespective of its scope                        of work or financial commitments.

- This Agreement shall     be construed and interpreted in accordance    with the Law sof India and                                                                                                                                                                                               courts at New Delhi alone shall have the exclusive jurisdiction in all matters relating thereto and arising there under.

- It is hereby further agreed that in case of being selected as the Successful Bidder, the Members do hereby agree that they shall furnish the Performance Guarantee in favour of COPA in terms of the RfS.

- It is further expressly agreed that the Agreement shall be irrevocable and shall form an integral part of the Power Purchase Agreement (PPA) and shall remain valid until the expiration or early termination of the PPA in terms thereof, unless expressly agreed to the contrary by COPA/COPA.

- The Lead Member is authorized and shall be fully responsible for the accuracy and veracity of the representations and information submitted by the Members respectively from time to time in the response to RfS.

- It is hereby expressly understood between the Members that no Member at any given point of time, may assign or delegate its rights, duties or obligations under the PPA except with prior written consent of COPA/COPA.

- This Agreement

  - has been duly executed and delivered on behalf of each Member hereto and constitutes the legal, valid, binding and enforceable obligation of each such Member;

  - sets forth the entire understanding of the Members hereto with respect to the subject matter here of; and

  - may not be amended or modified except in writing signed by each of the Members and with prior written consent of COPA/COPA.

- All the terms used in capitals in this Agreement but not defined herein shall have the meaning as per the RfS and PPA.

IN WITNESS WHEREOF, the Members have, through their authorized representatives, executed these present on the Day, Month and Year first mentioned above.

ForM/s	[Member1]

(Signature, Name & Designation of the person authorized vide Board Resolution Dated

) Witnesses:

1)Signature-----------------------

Name: Address:

2) Signature ---------------------

Name: Address:

ForM/s	[Member2]

(Signature, Name & Designation of the person authorized vide Board Resolution Dated

)

Witnesses:

1) Signature-------------------

Name:

Address:

ForM/s   _______[Membern]

(Signature, Name & Designation of the person authorized vide Board Resolution Dated

)

Witnesses:

1) Signature-----------------------

Name:

Address:

(2) Signature ----------------------

Name:

Address:

2) Signature ----------------------

Name:

Address:

Format 7.6

### FORMAT FOR FINANCIAL CAPABLITY

(To be submitted on the letterhead of Bidding Company)

To,

Cochin Port Authority

W/Island

Kochi-682009

Dear Sir,

Sub:		   Bid for  “------------------”  in response to the RfS No-------------------------

- We submit our Bid(s) for the total capacity of ……. kW (Insert total offered capacity in kW and submit details of our Financial Eligibility Criteria

We certify that the Financially Evaluated Entity (ies) had an Annual Turnover as follows:

The maximum Annual turnover of Rupees …….Crore per MW in any one of the last 3 financial years preceding the Bid Deadline subject to the condition that the Bidder should at least have completed one financial year .

OR

Net worth of Rs………Crore computed as per instructions provided in Clause 2.4.3. (Strike Out whichever Is Not Applicable)

Financial eligibility criteria

| Name of Financially Evaluated Entity* | Relationship with Bidding Company** | Financial year | Year of Incorporation of the Bidding company | ***Total Maximum Annual Turnover (Rs. Crore) | Net worth as per Clause 2.4.3 (in Rs. Crore) |
| --- | --- | --- | --- | --- | --- |

* The Financially Evaluated Entity may be the Bidding Company itself.

** The column for “Relationship with Bidding Company” is to be filled only in case financial capability of Parent Company and/or Affiliate has been used for meeting Qualification Requirements.

*** Bidder shall furnish maximum annual turnover in any of the last three financial years.

Yours faithfully

(Signature and stamp (on each page) of Authorized Signatory of Bidding Company. Name:

………………………….

Date:……………………………

Place:…………………………..

(Signature and stamp (on each page) of Chartered Accountant/Statutory Auditors of Bidding Company.

Name: ………………………….. Date: ……………………………. Place: ……………………………

Notes:

Audited  consolidated  annual  accounts  of  the  Bidder  may  also  be  used  for  the purpose of financial criteria provided the Bidder has at least 26% equity in each company whose accounts are merged in the audited  consolidated  accounts  and provided further  that the financial capability of such companies (of which accounts are being merged in the consolidated accounts) shall not be considered again for the purpose of evaluation of the Bid.

Format 7.7

FORMAT FOR DISCLOSURE

### (This should be submitted on the Letter Head of the Bidding Company/EachMember of the Consortium)

DISCLOSURE

Ref.No.		Date:

From:	(Insert name and address of Bidding Company)

Tel.#:

Fax#:

E-mail address#

To

Cochin Port Authority

W/Island

Sub: Response to RfS No. -------for  Selection of Solar Power Developers  for ----------------

.

Dear Sir/ Madam,

We hereby declare and confirm that only we are participating in the RfS Selection process for the RfSNo.	and that our Parent, Affiliate or Ultimate Parent or any Group Company with which we have direct or indirect relationship are not separately participating in this selection process.

We further declare that the above statement is true & correct. W ear aware that if at any stage it is found to be incorrect, our response to RfS will be rejected and if LoI has been issued or PPA has been signed, the same will be cancelled and the bank guarantees will be encashed and recoveries will be effected for the payments done.

Dated the	day of	, 20….

Thanking you,

We remain,

Yours faithfully,

Name, Designation, Seal and Signature of Authorized Person in whose name Power of Attorney/ Board Resolution/ Declaration.

Format 7.8

FORMAT FOR TECHNICAL CRITERIA

### (This should be submitted on the Letter Head of the Bidding Company/Lead Member of Consortium)

Ref.No.		Date:

From:	(Insert name and address of Bidding Company)

Tel.#:

Fax#:

E-mail address#

To

Cochin Port Authority

W/Island

Sub: Response to RfS No. F2---- Dated ---- for Selection of Solar Power Developers for-------------

Dear Sir/ Madam,

We hereby undertake to certify in line with Clause No.--, Section-II, ITB under the title “Financial Closure” that the following details shall also be furnished within 06 (Six) months of effective date of the PPA.

1.0	Evidence of achieving complete tie-up of the Project Cost through internal accruals or through a Financing Agency.

  - Evidence of clear possession of the required water body for the Project along with following documentary evidence:-

    - Ownership or lease hold rights (as per Clause 15, Section-II, ITB) in the name of the Solar Power Developer and possession of 100% of the area of location required for the Project.

    - Certificate by the concerned and competent revenue/ registration authority for the acquisition/ownership/righttouse/vesting of the are ainthe name of the Solar Power Developer.

    - Sworn affidavit/ any other agreement from the authorized signatory of the SPD listing the details of the location and certifying that total are arquired for the Project is under clear possession of the SPD.

    - A certified English translation from an approved translator in case above documents are in languages other than English and Hindi.

Failure or delay on our part in achieving he above conditions shall constitute sufficient grounds for encashment of our Performance Bank Guarantee.

Dated the	day of	, 20….

Thanking you,

We remain,

Yours faithfully,

Name, Designation, Seal and Signature of Authorized Person in whose name Power of Attorney/ Board Resolution/ Declaration.

Format 7.9

DECLARATION BY THE BIDDER FOR THE

PROPOSED TECHNOLOGY TIE-UP UNDER PART-B

| 1 | Name of Bidding Company/ Lead Member of Bidding Consortium |  |  |
| --- | --- | --- | --- |
| 2 | Name of the Technology Partner (if any) |  |  |
| 3 | Project Location |  |  |
| 4 | Capacity Proposed | ……………….. MW |  |
| 5 | Technology Proposed to be adopted for the Project |  |  |
| 6 | Estimated Annual Generation of Electrical Energy |  | kWh |
| 7 | Brief about the Proposed Technology |  |  |
|  | Crystalline Silicon Solar Cells and Modules |  |  |
|  | Concentrator PV Modules |  |  |
|  | Thin Film Modules |  |  |
|  | Any Other Technology |  |  |

Dated the_	day of	, 20…. Thanking you,

We remain, Yours faithfully,

Name,  Designation, Seal and Signature of Authorized Person in whose name Power of Attorney/ Board Resolution/ Declaration.

Format 7.10

FORMAT FOR SUBMISSION OF FINANCIAL BID

### (The Covering Letter should be submitted on the Letter Head of the Bidding Company/Lead Member of Consortium)

Ref.No.		Date:

From:	(Insert name and address of Bidding Company/Lead Member of Consortium)

Tel.#:

Fax#:

E-mail address#

To

Chief Mechanical Engineer

Cochin Port Authority

W/Island

Sub: Response to RfS No. ------- Dated =--- for --------------------------------

Dear Sir/ Madam,

I/We,	(Insert Name of the Bidder) enclose herewith the Financial Proposal for selection of  my/  our firm for	number of Project(s) for a cumulative capacity of MW in India as Bidder for the above.

I/We agree that this offer shall remain valid for a period of 240 (Two Hundred and Forty) days from the due date of submission of the response to RfS such further period as may be mutually agreed upon.

Dated the	day of	, 20….

Thanking you,

We remain, Yours faithfully,

Name, Designation, Seal and Signature of Authorized Person in whose name Power of Attorney/ Board Resolution/ Declaration.

### Notes:

      - There can be only one tariff for each project. If the bidder quotes two tariffs or combination there off or  a project, then the bid shall be considered as non-responsive.

      - If the bidder submits the financial bid in the Electronic Form at COPA portal not in line with the instructions mentioned therein, then the bid shall be considered as non- responsive.

      - TariffrequirementshallbequotedasafixedamountinIndianRupeesonly.Conditional proposal shall be summarily rejected.

      - Intheeventofanydiscrepancybetweenthevaluesenteredinfiguresandinwords,the values entered in words shall be considered.

      - Tariff should be in Indian Rupee up to two places of decimals only.

Format 7.11

PRELIMINARY ESTIMATE OF COST OF FLOATING

SOLAR POWER PROJECT

Project Capacity:	MW

| Sr. No. |  | Particulars |  | Estimated Cost (in Lakh INR) (in figures) |  | Estimated Cost (in Lakh INR) (in words) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1. | PV Modules |  |  |  |  |  |
| 2. | Area Cost/water body cost |  |  |  |  |  |
| 3. | Civil and General Works |  |  |  |  |  |
| 4. | Mounting Structures |  |  |  |  |  |
| 5. | Power Conditioning Unit |  |  |  |  |  |
| 6. | Evacuation Cost up to Inter-connecting point (Cables and Transformers) |  |  |  |  |  |
| 7. | Preliminary and Pre-Operative Expenses including IDC and Contingency |  |  |  |  |  |
| 8. | Others (Please specify) |  |  |  |  |  |
| 9. | Total Project Cost |  |  |  |  |  |

Dated the_	day of	, 20….

Thanking you,

We remain,

Yours faithfully,

Name, Designation, Seal and Signature of Authorized Person in whose name Power of Attorney/ Board Resolution/ Declaration.

Format 7.12

Selection of Solar Power Developers  for-----------------

ORGANIZATION DETAILS

| S. No | Particulars | Details |
| --- | --- | --- |
| 1 | Name of the Company |  |
| 2 | Registered Office Address |  |
| 3 | Telephone, Telex, Fax No |  |
| 4 | E-mail |  |
| 5 | Web site |  |
| 6 | Authorized Contact Person(s) with name, designation Address and Mobile Phone No., E-mail address/ Fax No. to whom all references shall be made |  |
| 7. | Year of Incorporation |  |
| 8 | Bidding company PAN Number |  |
| 9. | Bidding company TAN Number |  |
| 10. | Have the bidder/Company ever been debarred By any Govt. Dept. / Undertaking for undertaking any work. |  |
| 11. | Reference of any document information attached by the Bidder other than specified in the RFP. |  |
| 12. | Whether the Bidder wishes to form a Project Company for execution of work | Yes/No/May be |
| 13. | Bidding company is listed in India | Yes/No |
| 14. | Details of the Ownership structure (Details of persons owning 10% or more of the Total Paid up equity of the Bidding Company in the Format as below |  |
| 15. | Bid Bond Bank guarantee No |  |
| 16. | Validity of Bid Bond |  |
| 17. | - Banker E-mail ID, - FAX No of the banker - Correspondence address &Pin Code |  |

(Signature of Authorized Signatory) With Seal

Format 7.13

Selection of Solar Power Developers  for------------------

Tenderer shall furnish Details of “eligibility works experience” as per Minimum Eligible Criteria (MEC) of Instruction to Tenderer and certificates in the following format (Client Certificates/work completion certificates or any other documentary evidences with respect to the eligibility work)

ELIGIBLE ASSIGNMENT DETAILS FOR MQC

Assignment Number :

| Description | Bidder to fill up the details here |
| --- | --- |
| Name and Address of the Client |  |
| Title of the Eligible Assignment |  |
| Date of completion of the Eligible Assignment |  |
| Project Completion Cost |  |
| Reference No. of the enclosed Client Completion Certificate/ Documentary Evidence for having successfully completed the Eligible assignment |  |
| Name, telephone no, tele fax no and email address of the client’s representative |  |
| Description and Scope of Work |  |

Instructions:

- Bidders are expected to provide information in respect of Eligible Assignments in this Section.  The assignments cited must comply with the Minimum eligibility of the Instructions to Tenderers”.

- A separate sheet should be filled for each of the eligible assignments.

- The details are to be supplemented by documentary proof from the respective client /owner for having carried out such assignment duly certified by clients/ owner.

- The works indicated in this Annexure- 4 will be only being considered for evaluation. Mere submission of work completion certificate will not be considered as Eligible Assignments

- Original or notary certified copy of completion certificates of each work issued by the owner/ the responsible officers of the owner under whom he has executed such contracts shall be attached. The certificate shall invariably contain the following among other things.

- Details of work involved specifying the nature of work

- The completion cost of the work and

- Date of commencement ; and

- Date of completion of the work.

- If the experience in similar works is as a member of joint venture, notary attested copy of joint venture agreement in this respect shall be attached.

- If the experience in similar works is as a subcontractor, notary attested copy(s) of approval issued by the Employer(s) authorizing as a sub-contractor; in proof of the claim of the tenderer as a sub-contractor shall be attached.

- If the experience in similar work is in works executed in private sectors/organisations, the TDS certificate along with notary attested copy(s) work order and completion certificate.

- The tenderer is also obliged to produce the original of the certified copy(s) on request by the department.

Signature

(Authorised Signatory)

Format 7.14

Selection of Solar Power Developers  for____________

DETAILS OF PAST EXPERIENCE OF CONTRACTORS FOR SIMILAR WORKS

| Sl. No. | Name & Location of Project | Owner’s Complete address including TeleFax No. with contact Person | Value of Contract | Duration of Contract |  |  | Details of work including major items of work involved | Reference No. & Date of letter of intent & completion certificate enclosed |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Commen-cement date | Scheduled completion date | Actual completion date |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

Note: Bidder to enclose completion certificate issued by owner, certified by a Notary public or equivalent certifying authority.

SIGNATURE OF TENDERER

Format 7.15

Certificate of Relationship of Parent Company or Affiliate with the Bidding Company.

To,

Cochin Port Authority

W/Island

Kochi-682009

Dear Sir,

Sub:	Bid for Implementation of Grid connected Roof Top Solar PV System at Cochin Port Authority Pradesh

We hereby certify that M/s…………………,M/s…………………..,M/s…………….are the Affiliate(s) /Parent Company of the Bidding Company as per the definition of Affiliate/Parent Company as provided in this RFS and based on details of equity holding as on seven (7) days prior to the Bid Deadline.

The details of equity holding of the Affiliate/Parent Company/Bidding Company or vice versa as on seven (7) days prior to the Bid Deadline are given as below:

| Name of Bidding Company/ applicant company | Name of the Affiliate of the Bidding company/ Applicant company/ Name of the Parent Company of the Bidding Company | Name of the Company having common control on the Affiliate and the Bidding Company | Percentage of Equity Holding of Parent Company in the Bidding Company/ Applicant company |
| --- | --- | --- | --- |

*Strike out whichever is not applicable.

(Insert Name  and  Signature  of  Statutory  Auditor  or  practicing  Company Secretary of  the Bidder)

Format 7.16

Undertaking from the Financially Evaluated Entity or its Parent Company/ Ultimate Parent Company

(On the Letter Head of the Financially Evaluated Entity or its Parent Company/Ultimate Parent Company)

Name:

Full Address:

Telephone No.:

E-mail address:

Fax/No.:

To

Cochin Port Authority

W/Island

Kochi-682009

Dear Sir,

We refer to the RFP No………..dated………..for “-----------------------------”

“We have carefully read and examined in detail the RFP, including in particular, Clause

….of the  RFP,  regarding  submission  of  an  undertaking,  as  per  the  prescribed  Format of the RFP.

We confirm  that  M/s……………(Insert  name  of  Bidding  Company/)  has  been  authorized by us to use our Technical and or financial capability for meeting the Technical and or Financial Eligibility as specified in Clause….of the RFP referred to above.

We have also noted the amount of the Performance Guarantee required to be submitted as per Clause….of the RFP the ………………………..(Insert the name of the Bidding Company) in the event of it being selected as the Successful Bidder”.

In view of the above, we hereby undertake to you and confirm that in the event of failure of

…………..(Insert name of the Bidding Company) to submit the Performance Guarantee in full or in part at any stage, as specified in the RFP, we shall submit the Performance Guarantee not submitted by ………………………(Insert name of the Bidding Company)”.

We have attached hereto certified true copy of the Board Resolution Whereby the Board of Directors of our Company has approved issue of this Undertaking by the Company.

All the terms used herein but not defined, shall have the meaning as ascribed to the said terms under the RFP.

Signature of Managing Director/Authorised signatory

Common seal of ……………….has been affixed in my/our presence pursuant to Board of Director’s Resolution dated……………

WITNESS

……………………. (Signature)

Name…………………………… Designation……………………..

……………………. (Signature)

Name…………………………… Designation……………………..

Format 7.17

Selection of Solar Power Developers  for--------------------------------

DETAILS OF PROPOSED APPROACH & METHODOLOGY

Bidder shall furnish a detailed method statement (Technical Note) for carrying out of the works, along with a  construction programme [ Preferably in MS project / Primavera] showing sequence of operation and the time frame for various segments of temporary and permanent works.

Signature

(Authorised Signatory)

Format 7.18

Selection of Solar Power Developers  for --------------------

DECLARATION

We M/s (Name & address of the bidder) hereby declare that:-

1. All details regarding construction plant, temporary work and personnel for site organisation considered necessary and sufficient for the work have been furnished in the Annexure  7 and that such plant, temporary works and personnel for site organisation will be available at the site till the completion of the respective work.

2. No conditions are incorporated in the financial bid. In case any conditions are specified in the financial bid, the tender will be rejected summarily without making any further reference to the bidder.

3. We have not made any payment or illegal gratification to any persons/ authority connected with the bid process so as to influence the bid process and have not committed any offence under PC Act in connection with the bid.

4. We disclose with that we have * made / not made payments or propose to be made to any intermediaries (agents) etc in connection with the bid.

5. We do hereby confirm that no changes have been made in the tender document downloaded and submitted by  us for the above bid.  Port Tender document will be treated as authentic tender and if any discrepancy is noticed at any stage between the Port’s tender document and the one submitted by the tenderer, the Port’s document shall prevail.

Signature

(Authorised Signatory)

* Note: Delete whichever is not applicable.

Format 7.19

DETAILS OF THE PARTY OPTING FOR REFUND OF EMD THROUGH  E-PAYMENT SYSTEM

Name of the Party	:

Bank A/c No		:

Account type		:  (Savings / Current / Overdraft)

Bank Name		:

Branch			:

IFSC Code Number	: (11 digit code)

Centre (Location)	:

FAX No.		:

E-Mail ID		: (For forwarding information of remittance)

Mobile No		:

Signature

(Authorised Signatory)

Format 7.20

FORMAT FOR FURNISHING BANK INFORMATION FOR e-PAYMENT

| 1 | Name and full address of the beneficiary |  |
| --- | --- | --- |
| 2 | Credit Account No. (Should be full 14 digit) |  |
| 3 | Account Type (SB or CA or OD) |  |
| 4 | Name of the Bank |  |
| 5 | Branch (Full address with telephone No.) |  |
| 6 | MICR code (Should be 9 digit) |  |
| 7 | Telephone/Mobile/Fax No. of the beneficiary | Telephone : |
|  |  | Mobile : |
|  |  | Fax : |
| 8 | Cancelled Cheque |  |

Signature with seal

(Authorised Signatory)

Annexure - A

TECHNICAL SPECIFICATION OF GRID CONNECTED FLOATING SOLAR PV POWER SYSTEM AND OTHER COMPONENTS

The proposed project shall be commissioned as per the technical specifications given below:

- DEFINITION

The Grid Connected Floating Solar Photo Voltaic (PV) power plant of 1.5 MWp capacity consists of PV array, Module Mounting Structure, Power Conditioning Unit (PCU) consisting of Maximum Power Point Tracker (MPPT), Inverter and Controls & Protections, interconnect cables and switches. PV Array shall be mounted on a suitable structure. The PV system shall have a battery backup and all components of the Floating Solar PV plant with Battery Energy Storage System (BESS) as per the requirement as per relevant BIS/ IEC standards. The design and commissioning also shall be as per latest IEC/BIS standards.

### SITE DETAILS AND SITEASSESSMENT

Thefollowingaresomeofthetechnicalmeasuresrequiredtoensurequalityof the major components used in grid connected solar power Projects:

  - The 1.5 MW Floating Solar Power Plant shall be installed at  the Backwaters near CoPA’s Walkway Avenue between BOT junction and Kannangatt bridge at W/Island, Cochin Port Authority, Kerala.

  - Bidder shall note that already Site survey, Bathymetric study, water body characteristics, geo-technical investigations (on shore/off shore) etc., water properties (such as TDS content etc), depth of reservoir (Full Reservoir Level (FRL), Minimum Drawdown level (MDDL), Dead Storage level etc.,), variation in the depth of water reservoir, water flow rate / current, climatic conditions have been carried out during the previous contract awarded and cancelled, which may be used for this project, at the discretion of the SPD.

  - Claims and objections due to ignorance of site condition will not be considered after submission of the bid. Bidder shall fully acquaint himself so as  to the nature of work, location and other environmental conditions and necessary statutory approvals required for the commissioning of the 1.5 MWp floating solar project. The bidder shall be deemed to have independently obtained all the necessary information required for   the   submission of the bid.

  - Bidder should have visited and carefully examined the site and surroundings for development of Floating Solar PV project.

  - Bidder should acquaint himself of the statutory requirements / approvals essentially required for the successful implementation of the Floating Solar PV project from the authorities like KSERC, KSEBL and CEA , KCZMA and shall coordinate with Statutory Authorities along with CoPA and CoPA will issue necessary authorization/ letters to approach the statutory authorities.

### FLOATING SOLAR SYSTEM

3.1.	 SYSTEM DESCRIPTION:

A Grid Connected Floating Solar Photovoltaic (FSPV) System shall consist of mainly the following components but not limited to any other components and accessories required to install and commission the same.

- Solar panels consisting of adequate capacity of solar PV Modules of suitable rating.

- Module mounting structure.

- Floating system.

- Mooring and anchoring system.

- String monitoring units/ Junction boxes.

- Grid interactive Power Conditioning Unit with (PCU) of suitable rating along with MPPT mechanism.

- Inverter rated Transformer

- 11kV Transmission line

- Metering system.

- Earthing system and lightning protection

- Suitable Battery Energy Storage System for excess power storage as per requirements.

- IR/UV protected Cable and other accessories. DC and AC power cables of appropriate size with cable termination kit

- 11kV Breaker panel with necessary protection and metering

- Reverse Power Relay.

- The solar PV Project shall be compatible with the proposed Supervisory Control and Data Acquisition ( SCADA) and should be integrated with the software.

- Indoor 11kV switchgear panels including Vacuum Circuit Breakers, Current Transformers, Voltage Transformers, Relays and other accessories for complete protection at the point of interconnection.

- ABT  / SMART meters with all necessary metering rated CTs and PTs at the interconnecting substation as per CEA metering regulation 2006 as amended time to time and state metering code

- Any other equipment/ material, not mentioned but required to complete the solar power plant facilities in all respect.

- The design of Floating Solar system shall be certified by the Third Party accredited agencies competent to approve the design.

- The floating system shall be designed in such a way that it shall appropriately incorporate walking platforms for regular maintenance and inspection.

- Appropriate anchoring/ mooring system shall be designed to keep the floating platforms in position inorder to adopt tidal waves, wind and water level variations of the location. The same shall be designed to ensure that the Floating PV panels along with mounting structure always float on the surface of water.

### SOLAR PHOTOVOLTAIC MODULES (PVMODULES)

- The Design requirements of Photo Voltaic arrays PV including DC array wiring, electrical protection devices and earthing provisions shall confirm to IEC 62548.

- Modules installed shall use RF identification tag and contain the following information.

- Name of the manufacturer of the PV module.

- Name of the manufacturer of Solar Cells.

- Month & year of the manufacture (separate for solar cells and modules)

- Country of origin (separately for solar cells and module)

- Unique Serial No and Model No of the module

- Valid certification of PV module.

- Use of advanced cell technologies

- The Contractor shall try to maximize the output within the allocated area. The contractor shall employ the latest technology.

- Based on the technology employed, the contractor has to design Electrical System Features, Architecture and Structural requirement and the same shall be approved by CoPA Engineers.

- Standards and Codes

The PV Modules used in the grid solar power projects shall normally qualify the latest edition of the following IEC PV module qualification test/ equivalent BIS standards as specified below: -

| Standard | Description |
| --- | --- |
| IEC 63049 | Defines the process starting from shipments of components to the installation site and includes the transport, unpacking, racking, construction, module installation process and operation and maintenance of the PV system, |
| IEC 62446 - 1 | Defines the information and documentation required to hand over the customer following the installation of Grid connected PV system. It also describes the commissioning tests, inspection criteria and documentation for the safe installation and correct operation of the system. |
| IEC 61829 | ON-SITE measurement of Current-Voltage characteristics. This standard specifies procedures for on site measurement of flat plate Photo Voltaic array characteristics, the accompanying meteorological conditions and translating to Standard Test Conditions (STC) or other selected conditions. Measurement of PV array Current-Voltage (I-V) characteristics under actual on -site conditions. |
| IEC 62446-2 | System maintenance. Defines Preventive, Corrective and performance related Maintenance requirements and recommendations for Grid connected PV Systems. The procedure covers Basic maintenance of the System components and connections for reliability, safety and Fire prevention. |
| IEC 61724 - 1 | Out lines Terminology, Equipment and Methods for Performance monitoring and Analysis of Photo Voltaic (PV) Systems. Monitoring of Bifacial Systems. Irradiance Sensor requirements. Soiling measurement based on latest technology. |
| IEC 61724 - 2 | Photo Voltaic System Performance – Part – 2. Capacity Evaluation method. Defines the procedure for comparing the measured power produced against the expected power from a PV System. |

3.3 FLOATINGDEVICE

  - The floatation device should be manufactured from appropriate thermoplastic with suitable UV stabilizer or thermoset plastic with suitable UV stabilizer or any other suitable material which shall not effect the water quality or contaminate the water. The life of floatation device shall be able to sustain for a minimum period of 25 years without any discoloration.

  - Float system should be designed to withstand the maximum wind speed of the location as per Wind Zone Map of India and shall be able to withstand the weight of O&M Personnel, carrying Tools, the forces of nature such as wind, waves and water flow etc.

  - The material used for floatation device shall be chemically resistant to acid, lye, petrol and mineral oil etc.

  - The floatation device, when installed in the backwaters shall not restrict the air flow around the panels. In order to facilitate this, the design of the floatation device shall be such that appropriate voids and shall form an integral part of the floatation device design.

  - The Solar System shall confirm to the below mentioned standards, but  not limited and is free to adopt better standards established and acceptable to the employer.

Standards and Codes

| Sl. No. | Standards | Description |
| --- | --- | --- |
| 1 | ASTM D1693 (or equivalent ISO Standards) | Test for Environmental Stress Cracking of HDPE |
| 2. | ISO16770 | Stress cracking resistance of HDPE |
| 3. | ASTM D790 (or equivalent ISO Standards) | Standard Test Methods for Flexural Properties of Unreinforced and Reinforced Plastics and Electrical Insulating Materials |
| 4. | ISO 178 | Plastics -- Determination of flexural properties |
| 5. | ASTM D638, ISO 527 | Standard Test Method for Tensile Properties of Plastics |
| 6. | ASTM D695, ISO 604 | Standard Test Method for Compressive Strength Properties of Plastics |
| 7. | ISO16770 | Full Notch Creep Test (FNCT) |
| 8. | ASTM D2565 (or equivalent ISO Standards) | Standard Practice for Xenon-Arc Exposure of Plastic intended for outdoor Applications |
| 9. | ASTM D4329(or equivalent ISO Standards) | Standard Practice for fluorescent ultraviolet (UV) lamp apparatus exposure of plastics |
| 10. | ASTM G7/G7M-11(or equivalent ISO Standards) | Standard Practice for atmospheric environmental exposure testing of non-metallic |
| 11. | ASTM D1693-15 (or equivalent ISO Standards) | Standard Test Method for Environmental stress cracking of Ethylene plastics |
| 12. | ASTM D5397-07(2012) | Standard Test Method for Environmental stress crack resistance of polyolefin geo-membrane |

### 3.4 ANCHORING / MOORINGSYSTEM

  - The minimum Life of the Anchoring system shall be 25years.

  - The Anchors shall be sturdy enough to withstand wind speed at that location

  - Anchoring system shall be able to withstand the depth/level variation of water level

  - The materials used in the anchoring system shall not contaminate the back waters or affect the aquatic ecosystem.

  - The design of anchoring system shall be certified by an accredited national/ international lab to fulfill the above conditions.

  - The Anchoring/ Mooring system shall comply with latest edition of API RP 2SK or any applicable standards.

3.5 JUNCTION BOXES (JBs)

a. 	The junction boxes are to be provided in the PV array for termination of connecting cables. The J. Boxes (JBs) shall be made of GRP/FRP/Powder Coated Aluminum /cast aluminum alloy with full dust, water & vermin proof arrangement. All wires/cables must be terminated through cable lugs. The JBs shall be such that input & output termination can be made through suitable cable glands.

b. 	Copper bus bars/terminal blocks housed in the junction box with suitable termination threads Conforming to IP65 standard and IEC 62208 Hinged door with EPDM rubber gasket to prevent water entry. Single / double compression cable glands, Provision for earthing the box must be provided.

c. 	Each Junction Box shall have High quality Suitable Capacity Metal Oxide Varistors (MOVs) / SPDs, suitable Reverse Blocking Diodes. The Junction Boxes shall have suitable arrangement monitoring and disconnection for each of the groups

d. 	Suitable markings shall be provided on the bus bar for easy identification and the cable ferrules must be fitted at the cable termination points for identification

The junction boxes/ enclosures should be IP 65(for outdoor)/ IP 54 (indoor) and as per IEC 529 specifications

3.6 DC DISTRIBUTION BOARD:

a. DC Distribution Board to receive the DC output from the array field.

b. DC DBs shall have enclosure of dust & vermin proof conforming to IP 65 protection. The bus bars shall be made of copper of desired size. Suitable capacity MCBs/MCCB shall be provided for controlling the DC power output to the PCU along with necessary surge arrestors.

3.7 AC DISTRIBUTION BOARD:

a. AC Distribution Board (DB) shall control the AC power from PCU/ inverter, and should have necessary surge arrestors.

b. All switches and the circuit breakers, connectors should conform to IEC 60947/IS60947, part I.

c. The  change over switches, cabling work should be undertaken by the bidder as part of the project.

d. All the Panels shall be metal clad, totally enclosed, rigid, floor mounted, air - insulated, cubicle type suitable for operation on three phase / single phase, 415 or 230 volts, 50 Hz .

e. The panels shall be designed for minimum expected ambient temperature of 50 degrees Celsius, 80 percent humidity and dusty weather.

f. All indoor panels shall have protection of IP54 or better standards. All outdoor panels shall have protection of IP65 or better standards.

g. Should conform to latest Indian Electricity Act and rules.

### h. All the 415 or 230 volt AC devices / equipment like bus support insulators, circuit breakers, Surge Protection Devices, Voltage Transformers etc., mounted inside the switchgear shall be suitable for continuous operation .

### POWER CONDITIONERS / INVERTERS

### PCU / ARRAY SIZE RATIO:

### The combined wattage of all inverters shall be sufficient for achieving 1.5MWp solar generation under Standard Testing Conditions.

### Maximum c power point tracker shall be integrated in the PCU/inverter to maximize energy drawn from the array.

### PCU/ INVERTER:

As PV array produce direct current electricity, it is necessary to convert this direct current into alternating current and adjust the voltage levels to match the grid voltage. Conversion shall be achieved using an electronic Inverter and the associated control and protection devices. All these components of the system are termed the “Power Conditioning Unit (PCU)”. In addition, the PCU shall also house MPPT (Maximum Power Point Tracker), an interface between Solar PV array & the Inverter, the power conditioning unit/inverter should also be DG set interactive, if necessary. Inverter output should be compatible with the grid frequency. Typical technical features of the inverter shall be as follows:

- Switching devices: IGBT/MOSFET

- Controller Type: Microprocessor /DSP

- Nominal AC output voltage and frequency: 415V, 3 Phase, 50 Hz

- Output frequency: 50 Hz

- Grid Frequency Synchronization range shall be between 49.7Hz to 50.3Hz as per CEA Regulations 2010.

- Ambient temperature considered: -20o C to 50o C

- Humidity: 95 % Non-condensing

- Protection of Enclosure: IP54 (Min.) for indoor / IP-65(Min) for outdoor

- Grid Voltage tolerance: - 20% & + 15 %

- No-load losses: Less than 1% of rated power

- Inverter efficiency (minimum): >93%

- HD: < 3%

- PF: >0.95

- PCU/inverter shall be capable of complete automatic operation including wakeup, synchronization & shutdown.

- The output power factor of PCU inverter shall be suitable for all voltage ranges or sink of reactive power, inverter should have internal protection arrangement against any sustainable fault in feeder line and against the lightning on feeder.

- Built-in meter and data logger to monitor plant performance through external computer shall be provided.

- The power conditioning units / inverters should comply with applicable IEC/ equivalent BIS standard for efficiency measurements and environmental tests as per standard codes IEC 61683/IS 61683 and IEC 60068- 2(1,2,14,30) /Equivalent BIS Std.

- The charge controller (if any) / MPPT units environmental testing should qualify IEC 60068-2(1, 2, 14, 30)/Equivalent BIS Std.

- The PCU/ inverters should be tested from the MNRE approved test centers / NABL /BIS /IEC accredited testing- calibration laboratories. In case of imported power conditioning units, these shall be approved by any IACS certified testing lab.

    - INTEGRATION OF PV POWER WITH GRID:

The output power from PV would be fed to the inverters which converts DC produced by PV array to AC and feeds it into the 11kV grid of the 110kV substation of CoPA at Willingdon Island after synchronization. In case of grid failure, or low or high voltage, solar PV system shall be out of synchronization and shall be disconnected from the grid.

3.8.6 The Power Conditioners/Inverters of the PV power plants must conform to the latest edition of IEC/ equivalent BIS Standards as specified below:

| Efficiency Measurements | IEC 61683 |
| --- | --- |
| Environmental Testing | IEC 60068-2/ IEC 62093 |
| Electromagnetic Compatibility (EMC) | IEC 61000-6-2, IEC 61000-6-4 & other relevant parts of IEC 61000 |
| Electrical Safety | IEC 62103/ 62109-1&2/ IS 16221-1&2 |
| Protection against Islanding of Grid(Anti- Islanding Protection) | IEEE1547/IEC Standards 62116/ UL1741/ IS 16169 Or equivalent BIS |
| LVRT Compliance (Low voltage Ride Through) | As per the latest CERC Guidelines/ Order/ Regulations |
| Grid Connectivity | Relevant CERC Regulations (including LVRT Compliance) and Grid Code as amended and revised from time to time. |
| Rated capacity | Nominal/ Rated output power of the inverter (if different power ratings are mentioned at different temperatures, then power rating at 500 C shall be considered) in kW will be considered as inverter rated capacity. |
| Approved makes | As per MNRE / BIS list of approved makes |

3.9 	TRANSFORMER & METERING:

  - Dry/oil type relevant kVA, 415V /11kV, 50 Hz Step up Inverter rated Transformer along with all protections, switch gears, Vacuum circuit breakers, cables etc. along with required civil work. All the SS components shall be of SS304/ SS316 grade.

  - Transformers having 11 kV at HV side with breaker on LT and HT sides shall be used for stepping up the voltage to 11kV for the Solar Power Plant.

  - Transformers shall be of reputed make and should have relevant IS or international standards. Transformers shall have all relevant monitoring and protection devices as per the relevant Indian Standards/ International standards.

  - Rating of each transformer shall be standard type. The transformer manufacturer shall provide test certificates carried out on the transformers as per relevant IS standards. 11 kV Transformer shall conform to IS: 2026.

  - LV windings voltage is decided based on the inverter output voltage. The rating of transformer (kVA) is decided based on combined rating of Inverters.

  - The high voltage power from the transformers is routed through 11kV HT cable to 110kV substation

  - The bidirectional SMART meter (0.2 S class) shall be installed for the measurement of energy.

  - The bidder shall take approval/NOC from CEA (Central Electricity Authority) for the connectivity, technical feasibility, and synchronization of PV plant with distribution network and submit the same to CoPA before commissioning of PV plant.

3.10	PROTECTIONS

The system should be provided with all necessary protections like earthing, Lightning, and grid islanding as follows:

3.10.1	LIGHTNING PROTECTION

The PV power plants shall be provided with lightning & over voltage protection. The main aim in this protection shall be to reduce the over voltage to a tolerable value before it reaches the PV or other sub system components. The source of over voltage can be lightning, atmosphere disturbances  etc  The entire space occupying the PV array shall be suitably protected against Lightning by deploying required number of Lightning Arrestors. Lightning protection should be provided as per IS/IEC 62305 standard. The protection against induced high-voltages shall be provided by the use of metal oxide varistors (MOVs) and suitable earthing such that induced transients find an alternate route to earth.

3.10.2	SURGE PROTECTION

Internal surge protection shall consist of three MOV type surge-arrestors connected from +ve and –ve terminals to earth (via Y arrangement)

3.10.3	EARTHING PROTECTION

- Earth resistance shall not be more than 5 ohms. It shall be ensured that all the earthing points are bonded together to make them at the same potential.

3.10.4	GRID ISLANDING:

i. 	In the event of a power failure on the electric grid, it is required that any independent power-producing inverters attached to the grid turn off in a short period of time. This prevents the DC-to-AC inverters from continuing to feed power into small sections of the grid, known as “islands.” Powered islands present a risk to workers who may expect the area to be unpowered, and they may also damage grid-tied equipment. The PV system shall be equipped with islanding protection.

In addition to disconnection from the grid (due to islanding protection) disconnection due to under and over voltage conditions shall also be provided.

ii. A manual disconnect 4pole isolation switch beside automatic disconnection to grid would have to be provided at utility end to isolate the grid connection by the utility personnel to carry out any maintenance. This switch shall be locked by the utility personnel

3.10.5	HT EQUIPMENT

  - The 11 kV side equipment and parts shall be earthed as required under provisions of IS 3043. The system shall be designed with appropriate CTs & PTs to have all relevant protection. In addition, CTs and PTs shall also be provided for metering and protection purposes as elsewhere specified.

- The HT side shall have the following protections

Over current & earth fault relay with under voltage & over voltage protection under and over frequency protection relays.

- Reverse Power Relay shall be provided in 11kV VCB panel.

- The Solar PV system and associated power transmission system shall be protected as per relevant Indian Standards.

    - Earthing

Standards and Codes

Earthing system shall comply with latest revisions and amendments of the relevant IEC standards and IS codes. In particular, Earthing system shall comply with the following standards and codes.

| Standard/Code | Description |
| --- | --- |
| IS 3043 | Code of Practice for Earthing |
| IEEE 80 | IEEE Guide for Safety in AC Substation Grounding |
| IEEE 142 | IEEE Recommended Practice for Grounding of Industrial and Commercial Power Systems |

### Battery Energy Storage System (BESS)

Battery Energy Storage System (BESS) of required power and energy capacity of about 300 kW/ 300kWh, designed as per the load data given by CoPA, including unit batteries, Battery Management System (BMS), matching with Power Conditioning System (PCS), Step-up transformers, LT & HT switchgear panels, Auxiliary supply system, DC & AC power cables, control and communication cables, along with RTU and related accessories for communication, HVAC system, fire-fighting system and other related accessories.

### Codes and Standards:- The following codes or standards or its equivalent shall be followed for BESS as per the applicability:

| ### Standard/ (equivalent IS code) | ### Description |
| --- | --- |
| ### IEC 61427-2/IS 16270 | ### Secondary cells and batteries for renewable energy storage for On-grid applications |
| ### IEC 62485-2 | ### Safety requirements for secondary batteries and battery installations - to meet requirements on safety aspects associated with the erection, use, inspection, maintenance and disposal: Non-chemistry Specific (applicable to all secondary battery types) |
| ### IEC 61508 | ### Functional Safety of Electrical/Electronic/Programmable Electronic Safety-related Systems: Applicable for all Battery Energy Storage Systems |
| ### IEC 62133-1:2017 | ### Secondary cells and batteries containing alkaline or other non-acid electrolytes - Safety requirements for portable sealed secondary cells, and for batteries made from them, for use in portable applications - Part 1: Nickel systems |
| ### IEC 62133-2 :2017 | ### Secondary cells and batteries containing alkaline or other non-acid electrolytes - Safety requirements for portable sealed secondary cells, and for batteries made from them, for use in portable applications - Part 2: Lithium systems |
| ### IEC 62281/ UN 38.3 | ### Safety of primary and secondary lithium cells and batteries during transport: Applicable for storage systems using Lithium Ion chemistries |
| ### IEC 61850/DNP3 | ### Communications networks and management systems. (Plant SCADA and the BESS control system communication) |
| ### IEC TS 62933-5-1:2017 | ### Electrical energy storage (EES) systems - Part 5-1: Safety considerations for grid-integrated EES systems - General specification |

### For other technologies being used in ESS, the Developer shall adhere to the relevant environmental and safety standards issued by Government of India from time to time.

### Technical specification of BESS Table below specifies project-specific BESS capabilities and ratings for this Project

| ### Item Description | ### Requirement |
| --- | --- |
| ### Battery Technology | ### Any battery technology with totally Maintenance Free characteristic suitable for operation in site-specific climatic conditions can be used |
| ### Power rating*, AC (A), | ### 300kW(continuous) |
| ### Watt-hour rating, ac (B) | ### 300kWh, dispatchable at 300 kW net ac output at the beginning of life and not less than 80% of this capacity at any point of time. |
| ### System ac-dc-ac efficiency*: | ### 80% Use case requirements ### 1. Ramp Rate Support ### 2. Solar Power Integration into Distributed Generation Microgrid ### 3. Peak Management |
| ### Peak Management | ### In the Peak Management Use Case scenario, power generated during the early and midday periods shall be stored in the BESS and released later in the day, during peak demand. In this case, the BESS shall be discharged in the Peak Limiting profile in the late afternoon. To the extent that the total energy dispatched does not exceed the watt-hour rating, the BESS may be further discharged in Constant Power Mode after Solar PV Plant is no more generating. |
| ### Charge-Discharge Cycles | ### One discharge cycle per day is envisaged overall for all use cases, combined. However, based on the application, it may vary |
| ### VAR compensation /voltage support (VC/VS) | ### Yes, to support Distributed Generation |

### CABLES ANDCONNECTORS

All cables and connectors to be used for installation of solar field must be of solar grade which can withstand harsh environment conditions for 25 years and voltages as per latest IEC standards. The Cables of 600-1800 Volts DC for outdoor installations complying with the BIS/International Standards shall be used.

The cables laid in the water area shall be of submarine power cables conforming to IEC63026-2019. Cables should have adequate protection system to withstand the adverse environmental ondition of the site.

Cables of appropriate size to be used in the system shall have the following characteristics:

  - Shall meet IEC 60227/IS 694, IEC 60502/IS1554 standards

- Temp. Range: –10oC to +50oC.

- Voltage rating 660/1100VAC.

- Excellent resistance to heat, cold, water, oil, abrasion, UV radiation

- Flexible

- Sizes of cables between array interconnections, array to junction boxes, junction boxes to Inverter etc. shall be so selected to keep the voltage drop (power loss) of the entire solar system to the minimum. The cables (as per IS) should be insulated with a special grade PVC compound formulated for outdoor use.

- Cable Routing/ Marking: All cable/wires are to be routed through suitable cable tray arrangements to withstand the marine atmosphere tagged and marked with proper manner by good quality ferrule or by other means so that the cable can be easily identified.

- The Cable should be so selected that it should be compatible to the life of the solar PV panels i.e. 25years.

- The ratings given are approximate. Bidder has to indicate size and length as per system design requirement. All the cables required for the solar plant are to be provided by the bidder. All cable laying schedules/layout drawings shall be got approved prior to installation.

- Multi Stranded, annealed high conductivity copper conductor PVC type ‘A’ pressure extruded insulation or XLPE insulation. Overall PVC/XLPE insulation for UV protection Armored cable for underground laying. All cable trays including covers to be provided. All cables shall conform to latest edition of IEC/ equivalent BIS standards.

- Description Standard Number Cables General Test and Measuring Methods, PVC/XLPE insulated cables for working Voltage up to and including 1100 V, UV resistant for outdoor installation IS /IEC 69947.

- The size of each type of DC cable selected shall be based on minimum voltage drop however; the maximum drop shall be limited to 1%.

- The size of each type of AC cable selected shall be based on minimum voltage drop however; the maximum drop shall be limited to 2 %.

- DANGER BOARDS AND SIGNAGES:

Danger boards should be provided wherever necessary as per Indian Electricity Act/Rules as amended from time to time. The signages shall be provided at appropriate places. Text of the signage shall be approved by the employer.

- FIRE EXTINGUISHERS:

The firefighting system for the proposed power plant for fire protection shall be consisting of:

  - Portable fire extinguishers in the control room for fire caused by electrical short circuits

  - Sand buckets in the control room

  - The installation of Fire Extinguishers should confirm to BIS standards. The fire extinguishers shall be provided in the control room housing PCUs.

- DRAWINGS & MANUALS:

  - Six sets of Electrical drawings installation and O&M manuals shall be supplied. Bidders shall provide complete technical data sheets for each equipment giving details of the specifications along with make/makes in their bid along with basic design of the power plant and power evacuation, synchronization along with protection equipment.

- PLANNING AND DESIGNING:

  - The bidder should carry out Shadow Analysis at the site and accordingly design strings & arrays layout considering optimal usage of sunlight.

- The bidder shall submit preliminary drawing for approval & based on any modification or recommendation, if any. The bidder submits three sets and soft copy in CD of final drawing for formal approval to proceed with construction work.

8.	 DRAWINGS TO BE FURNISHED BY BIDDER AFTER AWARD OF CONTRACT

The Contractor shall furnish the following drawings and submit to CoPA after getting approval from third party inspection agency for approval

  - General arrangement and dimensioned layout

- Schematic drawing showing the requirement of PV panel, Power conditioning Unit(s)/ inverter, Junction Boxes, AC and DC Distribution Boards, meters etc.

- Structural drawing of the PV Array, Mounting Structure, Anchoring Arrangements and Foundation..

- Itemized bill of material for complete PV plant covering all the components and associated accessories.

- Layout of solar Power Array

- Shadow analysis of the area proposed

9.	SOLAR PV SYSTEM FOR MEETING THE ANNUAL ENERGY REQUIREMENT

Key Performance Indicators

### The contractor shall furnish monthly reports on above, without fail.

- PV Array Energy Yield

- Final System Yield

- PV System Efficiency (DC/AC)

- CO2 Savings

- Environment, Health & Safety

10. SAFETY MEASURES:

The bidder shall take entire responsibility for electrical safety of the installation(s) including connectivity with the grid and follow all the safety rules & regulations applicable as per Electricity Act, 2003 and CEA Regulation 2010 as amended from time to time.

11. Interface to the SCADA system:

The Solar panel Developer shall provide SCADA accessibility to the solar power plant  with SCADA proposed to be installed by CoPA under RDSS so as to monitor, control and rectify the faults immediately. Hardware and software used in solar power plant shall be in compliance with CEA cyber security guidelines/norms for power plant.

  - DATA ACQUISITION SYSTEM / PLANT MONITORING

- Data Acquisition System shall be provided for each of the solar PV plant. It shall be communicated with the proposed SCADA network of CoPA.

### SAFE DISPOSAL OF SOLAR PVMODULES

The SPD will ensure that all Solar PV modules, floats, and other components from their plant after their ‘end of life’ (when they become defective/ non-operational/ non-repairable) are disposed in accordance with the “e-waste (Management and Handling) Rules, 2011”notified by the Government and as revised and amended from time to time.

### STATUTORYAPPROVALS

Any neglect or omission or failure on the part of the bidder in obtaining necessary clearances and reliable information upon the forgoing or any other matter affecting the bid shall not relieve him from any risks or liabilities or the entire responsibility for completion of the work in accordance with the bid.

### RIGHT OFINSPECTION

- COPA reserves the right to inspect the components before dispatch at site.

(or) alternatively give dispatch clearance based on the testing & certification by third party Inspection agency. The cost of third party inspection shall be borne by the solar power developer and the third party inspection agency shall be got approved from CoPA before appointing them.

- COPA, reserves the right to witness Thirdparty test been performed by accredited testing laboratory in India.

- SPD shall provide access to COPA for monitoring the performance of the grid connected Floating Solar PV Project during the contract period.

- The SPDs shall provide access to COPA for installing any additional monitoring equipment to facilitate on-line transfer of data.

### SUBMISSION DETAILS

- The SPD shall provide/submit, free of cost to COPA all the Detailed Engineering Document with detailed specification, schematic drawing, circuit drawing, cable routing plans and test results, manuals for all deliverable items, Operation, Maintenance & Safety Instruction Manual and other information about the project, Bill of material, data etc.

Appendix - A1

COMMISSIONING PROCEDURE

(This is for Reference Only; The Commissioning Procedure will be guided by as per PPA)

- The plant shall be commissioned only on getting statutory approval for energization by CEA/ grid connectivity approval from KSEBL/SLDC.

- SPDs shall give to COPA at least 30 (Thirty) Days advance  written notice, of the date on which it intends to synchronize the Power Project to the Grid System. The SPD shall be solely responsible for any delay or non-receipt of the notice by the concerned agencies, which may in turn affect the Commissioning Schedule of the Project.

- A Solar PV Project will be considered as commissioned if all equipment as per rated project capacity has been installed and energy has flown into 11 kV  grid at 110 KV Substation located at Willingdon Island.

- SPD shall ensure that the equipment up to the rated Capacity has been installed and completed in all respects before the Scheduled Commissioning Date. The same shall be tested and certified by the Engineer in charge of the project.

### Documents to be submitted to COPA:

The SPD will have to submit the following documents (duly signed and stamped by authorized signatory) well in advance prior to the scheduled commissioning date. The SPD shall also have to submit the hardcopies to COPA if asked by COPA for verification/ cross check.

- Invoice(s) of the Major Equipment(s) (including but not limited to PV arrays, modules, Inverters/ PCUs, Transformers/ Cables and for all the equipment installed at the site.

- All supporting documents towards meeting the technical compliance along with datasheet/warrantycertificates/contractagreementetc.asmentionedinAnnexure-A(if some documents already verified by MNRE appointed committee prior to Financial Closure, may not be required which shall be updated on CPM portal)

- PlantLayoutclearlymentioningthedetailsofrowsandnumberofmodulesineachrow.

- Documents to be submitted to CEA for online application for the approval of 1.5 MWp Solar plant, CEA inspection report along with all annexures/ attachments and CEA compliance report ,Energisation report to CEA. .

- SPD shall ensure Connectivity to the grid.

- Supporting document for “Consent to Operate”

- Snap Shots of the Plant from various angles shall be taken for covering installation of important components of the solar power plant and made part of Installation Report.

- Reading of all the inverters (instantaneous and total generation) along with its serial number of a particular date.

- After the submission of the documents by SPD, COPA shall verify the documents and intimate/reply with remarks. In case any additional supporting/revised documents are asked by COPA, the same have to be submitted by the SPD.

- After the proposed commissioning date the Engineer-in charge will visit the site within 07 working days to verify the technical compliance on site as per the information submitted by the SPD. In case any deviation/ discrepancy has been observed from the information submitted by the SPD, the same shall be rectified and witnessed by the engineer – in charge and certified.

- SPD shall have to furnish the required plant related data to COPA’s designated server in suitable formats for accessibility. Additionally, SPD shall also provide the login details/SCADA login to COPA for online real time data monitoring. CEA cyber security rules shall be complied with before connecting the plant data to CoPA server.

- Early Commissioning of a Solar Project prior to the scheduled commissioning date is permitted on acceptance of power by COPA. Inorder to facilitate this,SPDs shall inform COPA well in advance the date on which it intends to synchronize the Power Project to the Grid System. The SPD shall be required to give an advance notice of atleast 30 days prior to the proposed commissioning date.

- Meter Reading shall be taken at the 110 KV Substation at the time of connectivity of the Project with Grid. This shall include information of respective meters installed at delivery/interconnection point.

- Solar Power Developers would be required to plan commissioning/synchronization with grid at least 10 (Ten) Days ahead of the last permissible date for commissioning.

Appendix - A2

INSTALLATION REPORT

(To be provided by SPD and to be submitted at least 10 days prior to Commissioning Date which

shall be verified by Commissioning Committee)

| Sr. No. | Capacity of the Project (MW) |  |
| --- | --- | --- |
|  | Capacity already commissioned (MW) |  |
|  | Capacity proposed to be commissioned (MW) |  |
| I. | Technology used (please specify along with capacity of each type) |  |
| II. | Rating of each module (Wp) |  |
| III. | Angle from horizontal at which array is installed |  |
| IV. | Number of modules installed of each type |  |
| V. | Source(s) of the cells installed of each type |  |
| VI. | Source(s) of the Modules installed of each type |  |
| VII. | Number of PCUs/ Inverters installed |  |
| VIII. | Source of the PCUs/ Inverters (Name of supplier with address) |  |
| IX. | Rating of PCUs/ Inverters |  |
| X. | Date of Installation of Full Capacity (as per Capacity proposed to be Commissioned) |  |
|  | PV Arrays |  |
|  | PCUs/ Inverters |  |
|  | Transformers |  |
|  | BESS : Storage technology . BESS rating ( Power& Energy with C rate and number of battery module pack. BESS : PCU ( Nos and ratings) OEM recommended DoD Unit Battery technical specification Nominal voltage Cut off voltage Battery cycle life ( at OEM recommended DoD) Operating temperatures |  |

Appendix - A3

SAMPLE CONNECTIVITY REPORT

(To be provided by concerned CTU/ STU/ Transmission Utility/ DISCOM)

This is in compliance to the office order of the-----,	DISCOM,<Place>issued vide office order

<No.><dated>,the committee constituted vide said order has completed the work for commissioning of<kV>Bay & Metering Equipment to inter connect the<MW>Solar Power Generation Plant (having <technology>)withGridinstalledat<Village>,<Tehsil>,<District>inthe<State>on<date>,under Rf SNo……………….dated………………..

The details of Solar Power Plant are as under:

| Sl. No | Name of Solar Power Developer &Location | Capacity Mentioned in PPA | Connectivity | Details of Solar Power Plant (Transformer, Inverter, Modules, Switchgear) |
| --- | --- | --- | --- | --- |
| 1 | <M/s> | <> MW | Metering Detail at Delivery Point (<Village>) S.No. of <kV> CT i) <R- Phase> ii) <Y-Phase> iii) <B- Phase> S.No. of < kV> PT i) <R- Phase> ii) <Y-Phase> iii) <B Phase> S.No. of Main<ABT> Meter>S.No. of Check <ABT Meter>S.No. of Standby <ABT Meter> Metering Equipment installed at Receiving end on dated: <> 132 kV GSS, <>, <>, (<Distt.>) | A) Transformer |
|  | <Village> |  |  | <Make/Type:> |
|  | <Tehsil> |  |  | <Sr. No.> |
|  | <District. |  |  | B) Inverters |
|  |  |  |  | <Make/Type:> |
|  |  |  |  | <Sr. No.> |
|  |  |  |  | C) Modules <Make:> |
|  |  |  |  | <W>, < W > |
|  |  |  |  | <Total: Nos.> |
|  |  |  |  | D) Switchgear |
|  |  |  |  | Panels |
|  |  |  |  | <Make/Type:> |
|  |  |  |  | <Sr. No.> |
|  |  |  |  | Protection Provided: |
|  |  |  |  | Under/Over voltage, |
|  |  |  |  | Over current & Earth fault. |

The Commissioning date of various equipment is as under:

<kV> line from --- to -----, completed on date -----.

Line Bay at < kV > GSS, ------ charged for ---- on -----.

<kV> line charged from ------to-------- on date	--.

Main & check metering commissioned on	(initial record of Main/Check meters at the time of

Commissioning is to be taken and enclosed) Complete system commissioned on date--------

The Joint Inspection Report of metering arrangement & copy of permission of Electrical Inspector is enclosed herewith.

Appendix - A4

SAMPLE SYNCHRONIZATION CERTIFICATE

It is certified that-----MW (Capacity)Floating Solar Photovoltaic Power project of M/s	,

Village-------Tehsil/Taluka--------,District----------was Grid connected on……….(Date)at----

Hrs.

It is further certified that the Project was synchronized and supply of power into the grid from the Project connectedon…………(Date)at	Hrs.

The above ertificate is issued on the basis of MRI record.

NB:

- The above certificate shall be issued by concerned STU/ SLDC/ KSEBL /CoPA

- Copy of duly signed MRI is to been closed.

Appendix - A5

SAMPLE PART COMMISSIONING/ FULL

COMMISSIONING CERTIFICATE OF FLOATING

SOLAR POWER PROJECT

This is to certify that<M/s>having its registered office at	has successfully commissioned

Capacity < MW > out of total <MW> installed Capacity on (Date) of their Solar PV Power Generation Project at Village ------, Tehsil/ Taluka ------- & Dist. ------

The Commissioning Certificate has been issued on the basis of the following documents enclosed:

  - Installation Report including Snap shots of the Project from various angles

  - Electrical Inspector Report

  - Connectivity Report

  - Synchronization Certificate including MRI record

NB:	TobeissuedbyasmentionedinClauseNo.16,Section-II,ITBofRfSDocuments.

Annexure - B

CHECK LIST FOR BANK GUARANTEES

| Sl. no. | Details of Checks | Yes/ No |
| --- | --- | --- |
| 1. | IstheBGonnon-judicialStamppaperofappropriatevalue,asperapplicable Stamp Act of the place of execution |  |
| 2. | Whether date, purpose of purchase of stamp paper and name of thepurchaserareindicatedonthebackofStampPaperundertheSignatureofStampvendor?(ThedateofpurchaseofstamppapershouldbenotlaterthanthedateofexecutionofBGandthestamp paper should be purchased either in the name of the executing Bank or the party on whose behalf the BG has been issued. |  |
| 3. | In case of BGs from Banks abroad, has the BG been executed on Letter Head of the Bank endorsed by the Indian branch of the same bank or SBI,India? |  |
| 4. | Has the executing Officer of BG indicated his name, designation and Power of Attorney No./ Signing Power no. on the BG? |  |
| 5. | IseachpageofBGdulysigned/initialedbyexecutantandwhetherstampofBankisaffixedthereon?Whetherthelastpageissigned with full particulars including two witnesses under seal of Bankas required in the prescribed proforma? |  |
| 6. | Do the Bank Guarantees compare verbatim with the Proforma prescribed in the Bid Documents? |  |
| 7. | Are the factual details such as Bid Document No./ Specification No./ LOI No. (if applicable)/ Amount of BG and Validity of BG correctly mentioned in the BG |  |
| 8. | Whether overwriting/ cutting, if any, on the BG have been properly authenticated under signature & seal of executant? |  |
| 9. | Whether the BG has been issued by a Bank in line with the provisions of Bidding documents? |  |
| 10. | In case BG has been issued by a Bank other than those specified in Bidding Document, is the BG confirmed by a Bank in India acceptable as per Bidding documents? |  |

Notes:

- TheStampPapershouldbeinthenameoftheExecutingBankandofappropriatevalue.

- ThePerformanceBankGuaranteeshallbeexecutedbyanyoftheBankfromtheListof Banks enclosed.

Annexure - C

LIST OF BANKS

| 1. SCHEDULED COMMERCIAL BANKS | 3. FOREIGN BANKS |
| --- | --- |
| SBI AND ASSOCIATES | 24. A B BANK |
| 1. State Bank of India | 25. SHINHAN BANK |
|  | 26. CTBC BANK Co. Ltd. |
| NATIONALISED BANKS | 27. MIZUHO BANK, Ltd. |
| 1. Allahabad Bank | 28. Krung Thai Bank Public Company Ltd. |
| 2. Andhra Bank | 29. Antwerp Diamond Bank N.V |
| 3. Bank of India | 30. Australia And New Zealand Banking Group Limited |
| 4. Bank of Maharashtra | 31. Sumitomo Mitsui Banking Corporation |
| 5. Canara Bank | 32. American Express Banking Corporation |
| 6. Central Bank of India | 33. Common Wealth Bank of Australia |
| 7. Corporation Bank | 34. Credit Suisse A.G |
| 8. Dena Bank | 35. FirstRand Bank Ltd. |
| 9. Indian Bank | 36. Industrial And Commercial Bank of China Ltd. |
| 10. Indian Overseas Bank | 37. JSC VTB Bank |
| 11. Oriental Bank of Commerce | 38. National Australia Bank |
| 12. Punjab National Bank | 39. Rabobank International |
| 13. Punjab & Sind Bank | 40. Sberbank |
| 14. Syndicate Bank | 41. USB AG |
| 15. Union Bank of India | 42. United Overseas Bank Ltd. |
| 16. United Bank of India | 43. Westpac Banking Corporation |
| 17. UCO Bank | 44. Woori Bank |
| 18. Vijaya Bank | 45. Doha Bank Qsc |
| 19. Bank of Baroda | 4. SCHEDULED PRIVATE BANKS |
| 2. OTHER PUBLIC SECTOR BANKS | 1. Federal Bank Ltd. |
| 1. IDBI Bank Ltd. | 2. ING Vysya Bank Ltd. |
| 3. FOREIGN BANKS | 3. Axis Bank Ltd. |
| 1. Bank of America NA | 4. ICICI Bank Ltd. |

| 2. Bank of Tokyo Mitsubishi UFJ Ltd. | 5. HDFC Bank Ltd. |
| --- | --- |
| 3. BNP Paribas | 6. Yes Bank Ltd. |
| 4. Calyon Bank | 7. Kotak Mahindra Bank |
| 5. Citi Bank N.A. | 8. IndusInd Bank Ltd. |
| 6. Deutsche Bank A.G | 9. Karur Vysya Bank |
| 7. The HongKong and Shanghai Banking Corpn. Ltd. | 10. Catholic Syrian Bank |
| 8. Standard Chartered Bank | 11. City Union Bank |
| 9. Societe Generale | 12. Dhanlaxmi Bank. Ltd |
| 10. Barclays Bank | 13. Jammu & Kashmir Bank Ltd |
| 11. Royal Bank of Scotland | 14. Karnataka Bank Ltd |
| 12. Bank of Nova Scotia | 15. Laxmi Vilas Bank Ltd |
| 13.Development Bank of Singapore (DBS Bank Ltd.) | 16. Nainital Bank Ltd |
| 14. Crédit Agricole Corporate and Investment Bank | 17. Ratnakar Bank Ltd |
| 15. Abu Dhabi Commercial Bank Ltd | 18. South Indian bank Ltd |
| 16. Bank of Bahrain & Kuwait B.S.C | 19. Tamilnadu Mercantile Bank Ltd |
| 17. Mashreq Bank p.s.c | 20. DCB Bank Ltd |
| 18. HSBC Bank Oman S.A.O.G | 21. IDFC Bank |
| 19. Sonali Bank Ltd. |  |
| 20. J. P. Morgan Chase Bank, National Association |  |
| 21. State Bank of Mauritius Ltd. |  |
| 22. BANK of CEYLON |  |
| 23. BANK INTERNATIONAL INDONESIA |  |

Annexure - D

SPECIAL INSTRUCTIONS TO BIDDERS FOR

e-TENDERING AND REVERSE AUCTION

### GENERAL

The Special Instructions (for e-Tendering) supplement ‘Instructions to Bidders’, as given in these Rfs Documents. Submission of Online Bids is mandatory for this RfS.

e-Tendering is a new methodology for conducting Public Procurement in a transparent and securedmanner.Now,theGovernmentofIndiahasmadee-Tenderingmandatory.Suppliers/ Vendors will be the biggest beneficiaries of this new system of procurement. For conducting electronic tendering, Cochin Port Authority(COPA)has decided to use the Portal of Government e-Marketing (https://gem.gov.in/).

Benefits to Suppliers are outlined on the Home-page of the portal.

### INSTRUCTIONS

Tender Bidding Methodology:

- View Notice Inviting Tender (NIT) on e tender portal

- Download Tender Documents from e tender portal

- Clarification to Tender Documents

  - Query to COPA(Optional)

  - View response to queries posted by COPA

- Bid-Submission one tender portal

- Respond to COPA Post-TOE queries

- ‘e-Reverse Auction’ if necessary. Participate in reverse auction if invited

### Some Bidding Related Information for this Tender

The entire bid-submission would be online on e tender portal. Broad outline of submissions are as follows:

- Submission of Bid-Parts

  - Envelope I(Technical-Bid)

  - Envelope II(Financial-Bid)

- Submission of digitally signed copy of Tender Documents/Addendum

In addition to the above, the bidders are required to submit certain document sphysically offline also as per Clause No.23.a,Section-II,ITBof RfS Documents, failing which the technical bids will not be opened.

Note:

  - The Bidder should also upload the scanned copies of all the above mentioned original documents as Bid-Annexures during Online Bid-Submission.

  - In case of any discrepancy between the values mentioned in figures and in words, the value mentioned in words will prevail.

  - Submit your bids well in advance of tender submission deadline on ETS (There could be last minute problems due to internet timeout, breakdown, etc.)

### ADDITIONAL DO’S AND DON’TS FOR BIDDERS PARTICIPATING IN e-REVERSEAUCTION

- Get your organization's concerned executives trained for e-Reverse Auction related processes on ETS well in advance of the start of e-Reverse Auction.

- For responding to any particular e-Reverse Auction, the e-Reverse Auction (ie its Reverse Auction Search Code or RASC) has to be obtained to the authorized person assigned by the bidder

- It is important for each bidder to thoroughly read the ‘rules and related criterion’ for the e- Reverse Auction as defined by the Buyer organization.

- It is important to digitally-sign your ‘Final bid’ after the end of e-Reverse Auction bidding event.

### Minimum Requirements at Bidder’s End

  - Computer System with good configuration (Min PIV, 1 GB RAM, Windows 7 and above)

  - Broadband connectivity

  - Microsoft Internet Explorer 7.0 or above

  - Registration to GeM portal

Annexure - E

TERMS & CONDITIONS OF REVERSE AUCTION ( If same price is quoted by more than 1 bidder in the ON LINE price bids)

AfteropeningofFinancialbidsandshort-listingofbiddersbasedonthetariffandtotalcapacity of project of qualified Project(s), COPA shall resort to “REVERSE AUCTION PROCEDURE” if required. Reverse Auction shall be conducted as per methodology specified in Section-V and other provisionsofReverseAuctioninRfSDocumentsandtheirsubsequentAddenda/Amendments/ Clarifications.Biddersintheirowninterest,areadvisedtogothroughthedocumentsinentirety. The Terms & Conditions and Business Rules mentioned hereunder are in brief and may not give completer explanations. Further these are supplementary in nature.

- Bidders shall ensure online submission of their ‘BidPrice’ within the auction period.

- Bidders shall ensure to take all necessary training and assistance before commencement of reverse auction to the interested bidders on chargeable basis to be paid directly to COPA.

- Business rules for Reverse Auction like event date, time, bid decrement, extension etc. shall be intimated later on, for compliance.

- Bidders should acquaint themselves of the ‘Business Rules of Reverse Auction’, which is enclosed separately in the RfS document.

- If the Bidder or any of his representatives are found to be involved in Price manipulation/ cartel formation of any kind, directly or indirectly by communicating with other bidders, action as per extant COPA guidelines, shall be initiated by COPA

- The Bidder shall not divulge either his Bids or any other exclusive details of COPA to any other party.

- Period of validity of Prices received through Reverse Auction shall be same as that of the period of validity of bids offered.

- Bidders should also note that:

  - Although extension time is ‘8’minutes, there is a time lag between the actual placing the bid on the local computer of the bidder and the refreshing of the data on to the server for the visibility to the Owner. Considering the processing time for data exchange and the possible network congestion, bidders must avoid the last minute hosting of the Financial Bid during reverse auction.

  - Participating bidder will agree to non-disclosure of trade information regarding the purchase, identity of COPA, bid process, bid technology, bid documentation and bid details.

  - It is brought to the attention of the bidders that the bid event will lead to the final price of bidders only.

  - Technical and other non-commercial queries ,Order finalization and post order activities such issue of LOI, signing of PPA etc. (not impacting price) ean only be routed to the COPA contact personnel indicated in the RfS document.

  - LOI shall be placed outside the COPA e-portal & further processing of the LOI shall also be outside the system.

  - In case of any problem faced by the bidder during Reverse Auction and for all Bidding process related queries, bidders are advised to contact the persons of M/s GEM indicated in Annexure - D of the RfS document.

  - Bidders are advised to visit the auction page and login into the system well in advance to identify/rectify the problems to avoid last minute hitches.

  - COPA will not be responsible for any PC configuration/ software/ hardware related issues, telephone line glitches and breakdown/ slow speed in internet connection of PC at Bidder’s end.

- No queries shall be entertained while Reverse Auction is in progress.

BUSINESS RULES OF REVERSE AUCTION

Reverse Auction shall be conducted as per methodology specified in Section - V and other provisions of Reverse Auction in RfS documents and their subsequent Amendments/ Clarifications/Addenda.Bidders,intheirowninterest,areadvisedtogothroughthedocuments in entirety.

The following would be parameters for e-Reverse Auction:

| Sl. No. | Parameter | Value |
| --- | --- | --- |
| 1. | Date and Time of Reverse-Auction Bidding Event | To be intimated Later to Eligible Bidders |
| 2. | Duration of Reverse-Auction Bidding Event | 1 Hour |
| 3. | Automatic extension of the ‘Reverse-Auction closing Time’, if last bid received is within a ‘Predefined Time-Duration’ before the ‘Reverse-Auction Closing Time’ | Yes |

| 3.1 | Pre-defined Time-Duration | 8 minutes |
| --- | --- | --- |
| 3.2 | Automatic extension Time-Duration | 8 minutes |
| 3.3 | Maximum number of Auto-Extension | Until there is no bid during the 8 minutes. |
| 5. | Entity-Start-Price | Tariff quoted by the bidders in Financial Bid (Second envelope) |

Online Reverse Auction shall be conducted by COPA on pre-specified date and time, while the bidders shall be quoting from their own offices/place of their choice. Internet connectivity shall have to be ensured by bidders themselves.

During the Reverse Auction, any requests for extension of time will not be considered by COPA. Bidder saret here fore requested to make all the necessary arrangements/ alternatives whatever required so that they are able to participate in the Reverse Auction successfully. Failure of power or loss of connectivity at the premises of bidders during the Reverse Auction cannot be the cause for not participating in the Reverse Auction. COPA shall not be responsible for such eventualities.

Bidders are advised to get fully trained and clear all their doubts such as refreshing of Screen, capacity/ no. of projects being auctioned, auction rules etc.

COPA reserves the right to cancel/ reschedule/ extend the Reverse Auction process/tender at any time, before ordering, without assigning any reason.

COPA shall not have any liability to bidders for any interruption or delay in access to the auction website irrespective of the cause. In such cases, the decision of COPA shall be binding on the bidders.

Other terms and conditions shall be as per bidder’s techno-commercial offers and as per the RfS document and other correspondences, if any, till date.

Annexure – F

Guidelines issued by Govt. of  Kerala for the installation of Energy Solar system

Department of Electrical Inspectorate

Office of the Chief Electrical Inspector

Housing Board Buildings,

Shanthi Nagar

Thiruvananthapuram- 695 001

Phone: 0471 2331104 , 0471 2331159

Email :cei@ceikerala.gov.in

Web site:www. ceikerala.gov.in

File No. B2 - 13958 / 2017 / CEI Thiruvananthapuram, 				Date: 24 / 07 / 2018.

CIRCULAR

Subject: 	Installation of Solar Energy System - guide lines issued – regarding

Reference: 	1. Circular No.B4-1750/14/CEI dated 09/01/2015.

2. Circular No. B4-1750/14/CEI dated 10/05/2016.

3. Letter No.B2-4335/16/CEI dated 10.05.2016.

4. Minutes of "Solar connect-distributed power generation through grid connected rooftop solar power plant programme stakeholders meeting" convened by the Additional Chief Secretary, Power department on 02/11/2016.

5. Provisions of the Electricity Act 2003, KSERC(Renewable energy and Net Metering Regulations) 2020.

6. Ministry of New and Renewable Energy (MNRE) notification dt:5/3/2020

For the effective implementation of Kerala Solar Energy Policy, 2013 the following guide lines are issued.

A. Guidelines for scrutiny / inspection of Solar Energy System

      - The minimum qualification for carrying out the installation work of a solar energy system shall be a A-Class Contractor licensee and depending up on the capacity of installation, eligible contractors can carry out the work. The bidder should possess valid ‘A Class’ Electrical Contractor’s License issued by any State/ Central licensing authority or the bidder should carry out the maintenance/electrical works through a licensed A Class contractor depending on the category of electrical installations. An undertaking to this effect shall be submitted in a stamp paper of Rs. 200/- while submitting the bid.

      - Verify whether the inverter is grid tied or not.

      - Inverter capacity shall be selected based on the solar PV generation, so that maximum generation can be utilized.

      - Solar PV module details such as number of modules, wattage, number of cells, voltage, current etc. shall be verified.

      - It has to be verified whether PV module shall be MNRE approved or not. If MNRE approved, their certificate of approval shall be verified. Otherwise certificate from MNRE approved lab shall be obtained.

      - It shall be verified that harmonics are within specified limit for grid tied systems.

      - Solar inverter details and its specifications shall be verified.

      - In the grid System, ensure that there is no back feeding to the grid when grid supply is off and anti islanding protection shall be ensured. Certificate from the manufacturer shall be obtained.

      - The adequacy of cable size for solar PV system shall be verified and ensured.

      - It shall be ensured that energy meter is provided for recording the solar energy generated.

      - If it is grid tied, it shall be ensured that Bi-directional meter (Net meter) is provided at the interconnection point to record the import and export of energy.

      - Solar panel supporting structures, inverter neutral, body etc. shall be earthed as per standards.

      - Breakers having adequate rating and surge protection device (SPD) shall be provided in the array junction box.

      - It shall be ensured that whether indicating meters are provided in DC and AC DBs .

      - Battery and inverter shall be segregated properly with fire proof partition.

      - If the proposed installation is having a DG set, reverse power relay shall be provided to avoid back feeding to DG set, if necessary.

      - While issuing sanction for energisation for Solar Energy System, following conditions are to be included in addition to normal conditions.

      - Consent from licensee shall be obtained (In case of grid tied system).

      - The whole installation should be in conformity with Central Electricity Authority (Technical Standards for connectivity of the distributed generation resources) Regulations, 2013 and Kerala State Electricity Regulatory Commission (Grid interactive distributed solar energy system) Regulations, 2014.

B. Important extracts of Central Electricity Authority (Technical Standards for connectivity of the distributed generation resources) Regulation, 2013(For information only)

5.11(1) 	Harmonic current injections from a generating station shall not exceed the limits specified in IEEE 519

5.11(2) 	The distributed generating resource shall not inject direct current greater than 0.5 % of the full rated output at the interconnection point

5.11(3) 	The distributed generating resource shall not introduce flicker beyond the limits specified in IEC 61000

7. 	The equipment of the generating station shall meet the following requirements.

        - Circuit breakers or other interrupting equipment shall be suitable for their intended application with the capability of interrupting the max available fault current expected at their location.

        - Distributed generation resource and associated equipment shall be designed so that the failure of any single device or component shall not potentially compromise the safety and reliability of the electricity system.

        - Paralleling device of distributed generation resource shall be capable of withstanding 220 % of the nominal voltage at the interconnection point.

8. 	Every time the generating station is synchronised to the electricity system, it shall not cause voltage fluctuation greater than ± 5 % at the point of connection 9. Provide a manually operated isolating switch between the distributed generation resource and the electricity system which shall meet following requirements.

  - Allow visible verification that separation has been accomplished.

  - Include indicators to clearly show open and closed positions.

  - Be capable of being reached quickly and conveniently 24 hrs a day by licensee's personnel without requiring clearance from the applicant.

  - Be capable of being locked in the open position.

  - May not be rated for load break nor may have features of over current protection

  - Be located at a height of at least 2.44 m above the ground level.

The SPD shall be conversant with KSERC (Renewable energy and net metering regulation) 2020 & its First amendment in 2022 as amended from time to time. The SPD shall comply with the above regulation for implementing the solar project.

C. Important extracts of Kerala State Electricity Regulatory Commission (Grid interactive distributed solar energy system) Regulation, 2014 (For information only)

4(2)(c) 	The solar energy system installed by the consumer shall be connected with interlocking system and operated safely in parallel with the distribution system of the licensee.

8(b) 	The interconnection of the solar energy system with the distribution system of the licensee conforms to the relevant provisions of the Central Electricity Authority (Measures relating to Safety and Electric Supply ) Regulations, 2010

8(c) 	The net meter and solar meter installed conform to the standards, specifications and accuracy class as provided in the Central Electricity Authority (Installation & Operation of Meters) Regulation, 2006.

9(1) 	The net meter shall be installed at the interconnection point of the eligible consumer with the network of the distribution licensee.

9(2) 	Solar meter shall be installed at the delivery point of the solar energy system to measure the solar electricity generated.

9(4) 	The meters shall be tested, installed and sealed.

11 	The eligible consumer shall comply with the specifications and standards and install grid - tied inverter, manually operated isolating switch and associated equipment with sufficient safe guards to prevent injection of electricity from his solar energy system to the distribution system of the licensee when the distribution system is de-energised.

13(12)

a. PV Module: Irradiance measurement, angle of inclination, temperature of the PV module and VI characteristics using PV Array Tester.

b. Solar Inverter: Efficiency, input voltage, output voltage, power, THD, DC injection flicker etc. and anti-islanding protection.

Sd/- Chief Electrical Inspector

Govt. of Kerala