DETAILED PROJECT REPORT

| Project: | Reconductoring of 11 KV Distribution lines in the areas of distribution of power supply by KDHPCL. |
| --- | --- |

INTRODUCTION

We have approximately 180 kilometers of Overhead High Tension 11 KV lines in our Distribution network supplying power to licensed distribution area of power supply. These lines were drawn long ago. Theses conductors are small and most of the conductors are Squirrel and Weasel type conductors. Over the years, these aged conductors have been exposed the nature under conditions of heavy rain and winds, etc. and have been damaged. Further our overhead lines are drawn through Company and Government Forest areas and hence damages due to trees falling over the lines cannot be avoided.

These old and aged distribution lines with narrow gauge and increased number of joints in the network had an adverse bearing on our line losses. Since 2000, we have been undertaking reconductoring works in our distribution network in a phased manner and as of date we have completed reconductoring works over 50 kms of the network. There has been a considerable reduction in the line breakdown and distribution line losses.

From our experience the reconductoring work has the following benefits:

- Reduction in line loss: Once the existing small conductors are replaced with newer lines with wider gauge, there will be reduction in the line losses in the said feeders and as a whole the net line loss in the system will also reduce.

- Stability of Line: With the new ACSR conductors we can expect more stability in the distribution system.

As part of our continued efforts in improving the quality of power supply, reliability and efficiency of the power distribution, we have planned to undertake the balance reconductoring works over the years in a phased manner.

TIME FRAME

We have completed around 50 kilometers of reconductoring in our distribution network. The pending areas for reconducting and the time frame for completion are detailed below.

| Sl No | Name of Feeder | Area to be reconductored |  | Length in kms to be reconductored | Prosed Time frame for work |
| --- | --- | --- | --- | --- | --- |
|  |  | From | To |  |  |
| 1 | Madupatty | Kundaly Dam | Chundavurrai Factory | 4.00 | 2022-2023 |
| 2 | Madupatty | Kundaly Dam | Chittavurrai Factory | 4.50 | 2022-2023 |
| 3 | ITD | ITD | Kalaar Factory | 5.00 | 2022-2023 |
| 4 | Nettigudi | Nettigudi | Guderale Factory | 4.00 | 2023-2024 |
| 5 | Nettigudi | Nettigudi | Devikulam | 5.00 | 2024-2025 |
| 6 | Nettigudi | Gudarale | Silent Valley | 2.00 | 2024-2025 |
| 7 | Nettigudi | Cigarette Point | Devikulam | 5.00 | 2025-2026 |
| 8 | Madupatty | Indo-Swiss | Arivikad | 2.00 | 2025-2026 |
| 9 | Madupatty | Madupatty | Thenmallay | 7.00 | 2026-2027 |
| 10 | Nettikudi | ODK | Periakanal | 5.00 | 2026-2027 |
|  |  | Total |  | 43.50 |  |

COST ESTIMATES

The size of the existing conductor used for drawing the 11 kV Overhead line is small and hence has less weight compared to the proposed conductors. The existing span length is high with average of around 70 meters. With the new ACSR conductors we need to reduce the span length in view of the increase in weight of the new conductors. Most of the existing posts are tubular or rail post and will not be suitable and needs replacement.

As such while estimating for reconducting we have factored this requirement. The proposed reconductoring work is inside the forest area. Since motorable access is limited, additional labour would be required for head loading the materials to site. Also, to ensure power supply is restored by 5.00 pm added labour will be needed to draw the line and complete the works as early as possible.

Based on our earlier experience in undertaking reconductoring works and considering the factors as stated above, we have prepared an estimate for one-kilometer reconductoring work as follows:

HT-Line Reconductoring cost per kilometre with Raccoon Conductor

| Sl. No. | Description | Unit | Qty | Rate in Rs. | Amount in Rs. |
| --- | --- | --- | --- | --- | --- |
| 1 | Angle Iron Post | No | 7 | 12,500 | 87,500 |
| 2 | HT Cross Arm | No | 7 | 1,200 | 8,400 |
| 3 | Disc Insulators | No | 12 | 650 | 7,800 |
| 4 | Pin Insulators | No | 12 | 125 | 1,500 |
| 5 | ACSR – 1 kms x 3 line | kgs | 1050 | 225 | 236,250 |
| 6 | GI Wire for earth | kgs | 50 | 100 | 5,000 |
| 7 | Stay Set | Nos | 10 | 2,500 | 25,000 |
| 8 | Transportation – Tractor with labour | LS |  |  | 30,000 |
| 9 | Labour Charge | LS |  |  | 50,000 |
| 10 | Earthing | No | 7 | 225 | 1,575 |
|  | Total |  |  |  | 453,025 |

It is assessed that for drawing one kilometer a minimum of seven (7) new posts on an average needs to be inserted in the existing line.

Approximate cost for reconductoring one kilometre with Raccoon ACSR conductors for 11kV HT-Line –Rs 4.5 lakhs.

BUDGETERY PROVISION

A summary of the works and the estimated cost of completion for each of the proposed work is as below:

| Sl No | Name of Feeder | Area to be reconductored |  | Length (kms) | Prosed Time frame for work | Amount in Rs. Lakhs | Detailed cost reference |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | From | To |  |  |  |  |
| 1 | Madupatty | Kundaly Dam | Chundavurrai Factory | 4.00 | 2022-2023 | 18.12 | Table 1 |
| 2 | Madupatty | Kundaly Dam | Chittavurrai Factory | 4.50 | 2022-2023 | 20.25 | Table 2 |
| 3 | ITD | ITD | Kalaar Factory | 5.00 | 2022-2023 | 22.51 | Table 3 |
| 4 | Nettigudi | Nettigudi | Guderale Factory | 4.00 | 2023-2024 | 18.12 | Table 4 |
| 5 | Nettigudi | Nettigudi | Devikulam | 5.00 | 2024-2025 | 22.51 | Table 5 |
| 6 | Nettigudi | Guderale | Silent Valley | 2.00 | 2024-2025 | 9.08 | Table 6 |
| 7 | Nettigudi | Cigarette Point | Devikulam | 5.00 | 2025-2026 | 22.51 | Table 7 |
| 8 | Madupatty | Indo-Swiss | Arivikad | 2.00 | 2025-2026 | 9.08 | Table 8 |
| 9 | Madupatty | Madupatty | Thenmallay | 7.00 | 2026-2027 | 31.58 | Table 9 |
| 10 | Nettigudi | ODK | Periakanal | 5.00 | 2026-2027 | 22.51 | Table 10 |
|  | Total |  |  | 43.50 |  | 196.27 |  |

^ Budgets have been prepared at the current cost levels.

| Table 1 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Project: | Rerouting and reconductoring of HT OH line from Kundaly Dam To Chunduvarrai Factory 4 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 28 | 12,500 | 350,000 |
| 2 | HT Cross Arm | Nos | 28 | 1,200 | 33,600 |
| 3 | Disc insulator | Nos | 48 | 650 | 31,200 |
| 4 | Pin | Nos | 48 | 125 | 6,000 |
| 5 | ACSR | Kgs | 4208 | 225 | 9,46,800 |
| 6 | GI Wire for earthing | Kgs | 200 | 95 | 19,000 |
| 7 | Stay set | Nos | 40 | 2500 | 100,000 |
| 8 | Transport charges |  |  |  | 120,000 |
| 9 | Labour charges |  |  |  | 200,000 |
| 10 | Earthing | Nos | 28 | 200 | 5,600 |
|  | Total |  |  |  | 18,12,000 |
| Table 2 |  |  |  |  |  |
| Project: | Rerouting and reconductoring of HT OH line from Kundaly Dam To Chittavurrai Factory 4.5 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 31 | 12,500 | 387,500 |
| 2 | HT Cross Arm | Nos | 31 | 1,200 | 37,200 |
| 3 | Disc insulator | Nos | 48 | 650 | 31,200 |
| 4 | Pin | Nos | 48 | 125 | 6,000 |
| 5 | ACSR | Kgs | 4734 | 225 | 10,651,150 |
| 6 | GI Wire for earthing | Kgs | 250 | 95 | 23,750 |
| 7 | Stay set | Nos | 43 | 2500 | 107,500 |
| 8 | Transport charges |  |  |  | 135,000 |
| 9 | Labour charges |  |  |  | 225,000 |
| 10 | Earthing | Nos | 31 | 200 | 6,200 |
|  | Total |  |  |  | 20,24,500 |
| Table 3 |  |  |  |  |  |
| Project: | Rerouting and reconductoring of HT OH line from Instant Tea Division To Kalaar Factory 5 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 35 | 12,500 | 437,500 |
| 2 | HT Cross Arm | Nos | 35 | 1,200 | 42,000 |
| 3 | Disc insulator | Nos | 60 | 650 | 39,000 |
| 4 | Pin | Nos | 60 | 125 | 7,500 |
| 5 | ACSR | Kgs | 5250 | 225 | 11,81,250 |
| 6 | GI Wire for earthing | Kgs | 250 | 95 | 23,750 |
| 7 | Stay set | Nos | 45 | 2500 | 113,400 |
| 8 | Transport charges |  |  |  | 150,000 |
| 9 | Labour charges |  |  |  | 250,000 |
| 10 | Earthing | Nos | 35 | 200 | 7,000 |
|  | Total |  |  |  | 22,51,400 |
| Table 4 |  |  |  |  |  |
| Project: | Rerouting and reconductoring of HT OH line from Nettigudi To Gudarale Factory 4 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 28 | 12,500 | 350,000 |
| 2 | HT Cross Arm | Nos | 28 | 1,200 | 33,600 |
| 3 | Disc insulator | Nos | 48 | 650 | 31,200 |
| 4 | Pin | Nos | 48 | 125 | 6,000 |
| 5 | ACSR | Kgs | 4208 | 225 | 9,46,800 |
| 6 | GI Wire for earthing | Kgs | 200 | 95 | 19,000 |
| 7 | Stay set | Nos | 40 | 2500 | 100,000 |
| 8 | Transport charges |  |  |  | 120,000 |
| 9 | Labour charges |  |  |  | 200,000 |
| 10 | Earthing | Nos | 28 | 200 | 5,600 |
|  | Total |  |  |  | 18,12,000 |
| Table 5 |  |  |  |  |  |
| Project: | Rerouting and reconductoring of HT OH line from Nettigudi To Devikulam 5 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 35 | 12,500 | 437,500 |
| 2 | HT Cross Arm | Nos | 35 | 1,200 | 42,000 |
| 3 | Disc insulator | Nos | 60 | 650 | 39,000 |
| 4 | Pin | Nos | 60 | 125 | 7,500 |
| 5 | ACSR | Kgs | 5250 | 225 | 11,81,250 |
| 6 | GI Wire for earthing | Kgs | 250 | 95 | 23,750 |
| 7 | Stay set | Nos | 45 | 2500 | 113,400 |
| 8 | Transport charges |  |  |  | 150,000 |
| 9 | Labour charges |  |  |  | 250,000 |
| 10 | Earthing | Nos | 35 | 200 | 7,000 |
|  | Total |  |  |  | 22,51,400 |
| Table 6 |  |  |  |  |  |
| Project: | Rerouting and reconductoring of HT OH line from Gudarale To Silent Valley 2 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 14 | 12,500 | 175,000 |
| 2 | HT Cross Arm | Nos | 14 | 1,200 | 16,800 |
| 3 | Disc insulator | Nos | 24 | 650 | 15,600 |
| 4 | Pin | Nos | 24 | 125 | 3,000 |
| 5 | ACSR | Kgs | 2100 | 225 | 472,500 |
| 6 | GI Wire for earthing | Kgs | 100 | 95 | 9,500 |
| 7 | Stay set | Nos | 20 | 2500 | 50,000 |
| 8 | Transport charges |  |  |  | 60,000 |
| 9 | Labour charges |  |  |  | 100,000 |
| 10 | Earthing | Nos | 28 | 200 | 5,600 |
|  | Total |  |  |  | 908,000 |
| Table 7 |  |  |  |  |  |
| Project: | Rerouting and reconductoring of HT OH line from Cigarrette point To Devikulam 5 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 35 | 12,500 | 437,500 |
| 2 | HT Cross Arm | Nos | 35 | 1,200 | 42,000 |
| 3 | Disc insulator | Nos | 60 | 650 | 39,000 |
| 4 | Pin | Nos | 60 | 125 | 7,500 |
| 5 | ACSR | Kgs | 5250 | 225 | 11,81,250 |
| 6 | GI Wire for earthing | Kgs | 250 | 95 | 23,750 |
| 7 | Stay set | Nos | 45 | 2500 | 113,400 |
| 8 | Transport charges |  |  |  | 150,000 |
| 9 | Labour charges |  |  |  | 250,000 |
| 10 | Earthing | Nos | 35 | 200 | 7,000 |
|  | Total |  |  |  | 22,51,400 |
| Table 8 |  |  |  |  |  |
| Project: | Rerouting and reconductoring of HT OH line from Indo-Swiss To Arvikad 2 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 14 | 12,500 | 175,000 |
| 2 | HT Cross Arm | Nos | 14 | 1,200 | 16,800 |
| 3 | Disc insulator | Nos | 24 | 650 | 15,600 |
| 4 | Pin | Nos | 24 | 125 | 3,000 |
| 5 | ACSR | Kgs | 2100 | 225 | 472,500 |
| 6 | GI Wire for earthing | Kgs | 100 | 95 | 9,500 |
| 7 | Stay set | Nos | 20 | 2500 | 50,000 |
| 8 | Transport charges |  |  |  | 60,000 |
| 9 | Labour charges |  |  |  | 100,000 |
| 10 | Earthing | Nos | 28 | 200 | 5,600 |
|  | Total |  |  |  | 908,000 |
| Table 9 |  |  |  |  |  |
| Project: | Rerouting and reconductoring of HT OH line from Madupatty To Thenmallay 7 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 49 | 12,500 | 612,500 |
| 2 | HT Cross Arm | Nos | 49 | 1,200 | 58,800 |
| 3 | Disc insulator | Nos | 84 | 650 | 54,600 |
| 4 | Pin | Nos | 84 | 125 | 10,500 |
| 5 | ACSR | Kgs | 7350 | 225 | 16,53,750 |
| 6 | GI Wire for earthing | Kgs | 350 | 95 | 33,250 |
| 7 | Stay set | Nos | 65 | 2500 | 163,800 |
| 8 | Transport charges |  |  |  | 210,000 |
| 9 | Labour charges |  |  |  | 350,000 |
| 10 | Earthing | Nos | 49 | 200 | 11,025 |
|  | Total |  |  |  | 31,58,225 |
| Table 10 |  |  |  |  |  |
| Project: | Rerouting and reconductoring of HT OH line from ODK To Periakanal 5 KM |  |  |  |  |
| Sl. No | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.) |
| 1 | Posts | Nos | 35 | 12,500 | 437,500 |
| 2 | HT Cross Arm | Nos | 35 | 1,200 | 42,000 |
| 3 | Disc insulator | Nos | 60 | 650 | 39,000 |
| 4 | Pin | Nos | 60 | 125 | 7,500 |
| 5 | ACSR | Kgs | 5250 | 225 | 11,81,250 |
| 6 | GI Wire for earthing | Kgs | 250 | 95 | 23,750 |
| 7 | Stay set | Nos | 45 | 2500 | 113,400 |
| 8 | Transport charges |  |  |  | 150,000 |
| 9 | Labour charges |  |  |  | 250,000 |
| 10 | Earthing | Nos | 35 | 200 | 7,000 |
|  | Total |  |  |  | 22,51,400 |

YEAR WISE SUMMARY OF CAPITAL SPEND

| Sl No | Year of Reconductoring | Kms to be reconductored | Budget Proposed in Rs. Lacs |
| --- | --- | --- | --- |
| 1 | 2022-2023 | 13.50 | 60.88 |
| 2 | 2023-2024 | 4.00 | 18.12 |
| 3 | 2024-2025 | 7.00 | 31.59 |
| 4 | 2025-2026 | 7.00 | 31.59 |
| 5 | 2026-2027 | 12.00 | 54.09 |
|  | Total | 43.50 | 196.27 |

COST BENEFIT ANALYIS

This exercise is needed to keep the distribution system in good condition and to avoid breakdown. This will also improve the quality and reliability of power supply in the distribution area. Further, this will definitely help us reduce the distribution losses in our network.

CONCLUSION

There is need to change the conductors in the distribution system in view its age, damages sustained over the years and the size to reduce the line loss.

We humbly request the Hon. Commission to kindly approve the Capital Investment Plan to undertake the reconductoring in the next five years as stated above.