## R&M 22-27
ANNEXURE C-Planning of Major Repair and Maintenance projection from FY 2022-2023 to FY 2026-2027
S.No | Description of works | Frequency | Estimated amount in Rs | 22-2023 | 23-2024 | 24-2025 | 25-2026 | 26-2027 | Remarks | Next Due on
1 | EHT Sub station Earthing System Healthiness check up | Once in 5 years | 225000 |  |  | 225000 |  |  |  | 2029-2030
2 | Repainting of Transformers, panel boards etc | Once in 5 years | 500000 |  |  |  |  | 550000 |  | 2031-2032
3 | Condition monitoring of Distribution Transformers (above 1MVA) | Once in 5 years | 100000 | 100000 | [5 empty] | 2027-2028
4 | EHT Substation relay coordination and Arc Flash intensity check up | Once in 5 years | 300000 |  |  | 300000 |  |  |  | 2029-2030
5 | OLTC servicing & oil replacement of EHT Power and distibution Transformers | Once in 3 years | 400000 |  | 440000 |  |  | 484000 | Service Bench mark - Every 5000 tap changing operations | 2029-2030
6 | Condition monitoring of EHT Power Transformers and Auxiliaries ( Year of commissioning - 2005) | Once in 3 years | 385000 | 385000 |  |  | 423500 |  |  | 2028-2029
7 | Testing and servicing of 3 Nos SF6 Circuit breaker in 110 KV substation | Once in 3 years | 75000 | 75000 |  |  | 82500 |  |  | 2028-2029
8 | Testing and servicing of 2 No.s VCB In SDF 17 | Once in 3 years | 40000 | 40000 |  |  | 42000 |  |  | 2028-2029
9 | Testing and servicing of 1 No.s VCB In SDF 3 | Once in 3 years | 80000 |  |  | 80000
10 | Testing and servicing of 1 No.s VCB In SDF 43 | Once in 3 years | 20000 | 20000 |  |  | 21000 | 0 |  | 2028-2029
11 | Testing and servicing of HT VCB's at 110 KV Substation - Section A | Once in 2 Years | 120000 | 126000 |  |  | 138600 |  |  | 2028-2029
12 | Testing and servicing of HT VCB's at 110 KV Substation - Section B | Once in 2 Years | 120000 |  | 126000 |  |  | 132300 |  | 2029-2030
13 | EHT Power Transformer oil filtration (12.5 MVA - 2 No's) | Once in 2 Years | 90370 | 94888.5 |  | 99632.925 |  | 104614.5713 |  | 2027-2028
14 | Distribution Transformers Oil Filtration ( 8 No's capacity up to 1250 KVA ) | Once in 2 Years | 50000 |  | 52500 |  | 55125 |  |  | 2027-2028
15 | EHT Power Transformers , Distribution Power Transformer and RMU's Protection relays testing | Once in 2 Years | 157500 | 157500 |  | 165375 |  | 173643.75 |  | 2028-2029
16 | Servicing & Refilling of fire extinguishers | Once in a year | 25000 | 26250 | 27562.5 | 28940.625 | 28940.625 | 30387.6562 |  | 2027-2028
17 | Power & Distribution Transformers Silica gel replacement | Once in a year | 10000 | 10500 | 11025 | 11576.25 | 11576.25 | 12155.0625 |  | 2027-2028
18 | Procurement of 05 No's SMPS used in Schneider make Energy meter | One Time | 10000 | 10000
19 | Replacement of Siemens make 3Nos. SIPROTEC Numerical Protection Relays at 110KV Substation | One Time | 295000 | 620000 | 310000 |  |  |  | Deterioration effecting the relay performance -2 Nos of relay replacing for planned in 22-23 (11Kv panel incomer side) and 1 No. in 23-24 (110KV control panel Transformer-1 incomer side) |  | 620000
20 | Replacement of 3 Nos. 200/5 A 2 core ( Protection & metering) in 11 KV VCB panel | One Time | 60000 | [5 empty] | Spare Purchase
21 | Replacement of cooling fins of old 500 KVA Transformer in Water Treatment Plant. | One Time | 200000 |  |  |  |  | 220000 | Severe rusting noticed on fins during periodical inspection
22 | Supply, Installation, testing and Commissioning of 5 No's 4 Pole, 250 A in existing LT Panel,SDF-16 | One Time | 200000 |  |  | 220000 |  |  | As a part of Condition based maintenance
23 | Replacement of Old aged 800A ACB in ring | One Time | 250000 |  | 250000 |  |  |  | As a part of Condition based maintenance
24 | Replacement of Old aged 800A ACB in SDF 16 | One Time | 250000 |  |  | 250000 |  |  | As a part of Condition based maintenance
25 | Outdoor RMU Hood replacememt Phase 1 | One Time | 325000 |  | 325000 |  |  |  | As a part of Condition based maintenance
26 | Outdoor RMU Hood replacememt Phase 2 | One Time | 350000 |  |  |  | 350000 |  | As a part of Condition based maintenance
27 | Outdoor RMU Hood replacememt Phase 3 | One Time | 350000 |  |  |  | 350000 |  | As a part of Condition based maintenance
28 | Protective relays replacement in Distributions panels (RMU's SDF-16,17,43 & warehouse cum office)-Phase 1 & 2 | One Time | 200000 |  | 210000 | 220500 |  | 0 | As a part of Condition based maintenance
29 | Replacement of deteriorated ACB and accssories at Plot No 30 CSEZ, Kakkanad | One Time | 375000 | 375000 |  |  |  |  | As a part of Condition based maintenance
30 | Procurement of 10 No's SMPS used in Schneider make Energy meter | One Time | 20000 |  | 20000
31 | Replacement of VCB panel in SDF-43, CSEZ, Kakkanad | One time | 525000 |  |  | 525000 |  |  | As a part of Condition based maintenance
32 | Replacement of VCB panel in Plot No.30, CSEZ, Kakkanad | One Time | 5250000 |  | 525000
33 | Calibration and Servicing of lab Equipments | Once in 3 years | 150000 | 150000 |  |  | 165000
34 | Substation water proofing | One Time | 750000 | 750000
35 | Consumption of Spares | Every year | 80000 | 80000 | 80000 | 80000 | 80000 | 80000
Total |  |  |  | 3020138.5 | 2377087.5 | 2206024.8 | 1748241.875 | 1787101.04

## R&M 22-27 year
ANNEXURE C-Planning of Major Repair and Maintenance projection from FY 2022-2023 to FY 2026-2027
S.No | Description of works | Frequency | Estimated amount in Rs. | Remarks | Next Due on
1 | Condition monitoring of Distribution Transformers (above 1MVA) | 5 Years | 100000 |  | 2027-2028
2 | Condition monitoring of EHT Power Transformers and Auxiliaries ( Year of commissioning - 2005) | 3 Years | 385000 |  | 2028-2029
3 | Testing and servicing of 3 Nos SF6 Circuit breaker in 110 KV substation | 3 Years | 75000 |  | 2028-2029
4 | Testing and servicing of 2 No's VCB In SDF 17 | 3 Years | 40000 |  | 2028-2029
5 | Testing and servicing of 1 No's VCB In SDF 43 | 3 Years | 20000 |  | 2028-2029
6 | Testing and servicing of HT VCB's at 110 KV Substation - Section A | 2 Years | 126000 |  | 2028-2029
7 | EHT Power Transformer oil filtration (12.5 MVA - 2 No's) | 2 Years | 94889 |  | 2027-2028
8 | Servicing & Refilling of fire extinguishers | 1 Year | 26250 |  | 2027-2028
9 | Power & Distribution Transformers Silica gel replacement | 1 Year | 10500 |  | 2027-2028
10 | Procurement of 5 No's SMPS used in Schneider make Energy meter | One Time | 10000 |  | NA
11 | Replacement of Siemens make 3Nos. SIPROTEC Numerical Protection Relays at 110KV Substation | One Time | 620000 |  | NA
13 | Replacement of deteriorated ACB and accessories at Plot No 30 CSEZ, Kakkanad | One Time | 375000 |  | NA
14 | Protective relay testing of EHT Power Transformers , Distribution Power Transformer and RMU's . | 2 Year | 157500 |  | 2028-2029
15 | Calibration and servicing of lab equipments | 3 Years | 150000 |  | 2025-2026
16 | Substation water proofing | One Time | 750000
17 | Consumption of Spares | Every year | 80000
| FY 2022 -23 Total |  | 3020139
Major R&M works FY 2023-2024
1 | OLTC servicing & oil replacement of EHT Power and Distribution Transformers | 3 Years | 440000 |  | 2026-2027
2 | Testing and servicing of HT VCB's at 110 KV Substation - Section B | 2 Years | 126000 |  | 2026-2027
3 | Distribution Transformers Oil Filtration ( 8 No's capacity up to 1250 KVA) | 2 Years | 52500 |  | 2025-2026
4 | Servicing & Refilling of fire extinguishers | 1 Year | 27563 |  | 2024-2025
5 | Power & Distribution Transformers Silica gel replacement | 1 Year | 11025 |  | 2024-2025
6 | Replacement of Siemens make 3Nos. SIPROTEC Numerical Protection Relays at 110KV Substation | One Time | 310000 |  | NA
7 | Outdoor RMU Roofing sheet and structure replacement Ring 1 | One Time | 325000 |  | NA
8 | Protective relays replacement in Distributions panels (RMU's SDF-16,17,43 & warehouse cum office)-Phase 1 | One Time | 210000 |  | NA
9 | Replacement of deteriorated 800A ACB in ring | One Time | 250000 |  | NA
10 | Procurement of 10 No's SMPS used in Schneider make Energy meter |  | 20000 | Subject to the condition of approval for new energy meters SITC | NA
11 | Replacement of VCB panel in Plot No.30, CSEZ, Kakkanad | One Time | 525000
12 | Consumption of Spares | Every year | 80000
| FY 2023 -24 Total |  | 2377088
Major R&M works FY 2024-2025
1 | EHT Sub station Earthing System Healthiness check up | 5 Years | 225000 |  | 2029-2030
2 | EHT Substation relay coordination and Arc Flash intensity check up | 5 Years | 300000 |  | 2029-2030
3 | Testing and servicing of 1 No's VCB In SDF 3 | 3 Years | 80000 |  | 2027-2028
4 | EHT Power Transformer oil filtration (12.5 MVA - 2 No's) | 2 Years | 99632.925 |  | 2026-2027
5 | EHT Power Transformers , Distribution Power Transformer and RMU's Protection relays testing | 2 Year | 165375 |  | 2026-2027
6 | Servicing & Refilling of fire extinguishers | 1 Year | 28940.625 |  | 2025-2026
7 | Power & Distribution Transformers Silica gel replacement | 1 Year | 11576.25 |  | 2025-2026
8 | Supply, Installation, testing and Commissioning of 5 No's 4 Pole, 250 A in existing LT Panel,SDF-16 | One Time | 220000 |  | NA
9 | Replacement of Deteriorated 800A ACB at SDF 16 | One Time | 250000 |  | NA
10 | Protective relays replacement in Distributions panels (RMU's SDF-16,17,43 & warehouse cum office)-Phase 2 | One Time | 220500 |  | NA
11 | Replacement of VCB panel in SDF-43, CSEZ, Kakkanad | One Time | 525000
12 | Consumption of Spares | Every year | 80000
| FY 2024 -25 Total |  | 2206024.8
Major R&M works FY 2025-2026
1 | Condition monitoring of EHT Power Transformers and Auxiliaries | 3 Years | 423500 | Year of commissioning - 2005 | 2028-2029
2 | Testing and servicing of 3 Nos SF6 Circuit breaker(2500A,145KV) at 110 KV substation | 3 Years | 82500 |  | 2028-2029
3 | Testing and servicing of 2 No's VCB(800A) at SDF 17 | 3 Years | 42000 |  | 2028-2029
4 | Testing and servicing of 1 No's VCB(630A) at SDF 43 | 3 Years | 21000 |  | 2028-2029
5 | Testing and servicing of HT VCB's at 110 KV Substation - Section A | 2 Years | 138600 |  | 2027-2028
6 | Distribution Transformers Oil Filtration ( 8 No's capacity up to 1250 KVA) | 2 Years | 55125 |  | 2027-2028
7 | Servicing & Refilling of fire extinguishers | 1 Year | 28940.625 |  | 2026-2027
8 | Power & Distribution Transformers Silica gel replacement | 1 Year | 11576.25 |  | 2026-2027
9 | Outdoor RMU Roofing sheet and structure replacement Ring 2 & Ring 3 | One Time | 700000 |  | NA
10 | Calibration and servicing of lab equipments | 3 years | 165000
11 | Consumption of Spares | Every year | 80000
| FY 2025 -26 Total |  | 1748241.875
Major R&M works FY 2026-2027
1 | Repainting of Transformers, panel boards etc. | 5 Years | 550000 |  | 2031-2032
2 | OLTC servicing & oil replacement of EHT Power and Distribution Transformers | 3 Years | 484000 |  | 2029-2030
3 | Testing and servicing of HT VCB's (1250A,11KV)at 110 KV Substation - Section B | 2 Years | 132300 |  | 2028-2029
4 | EHT Power Transformer oil filtration (12.5 MVA - 2 No's) | 2 Years | 104614.5713 |  | 2028-2029
5 | EHT Power Transformers , Distribution Power Transformer and RMU's Protection relays testing | 2 Year | 173643.75 |  | 2028-2029
6 | Servicing & Refilling of fire extinguishers | 1 Year | 30387.6562 |  | 2023-2024
7 | Power & Distribution Transformers Silica gel replacement | 1 Year | 12155.0625 |  | 2023-2024
8 | Replacement of cooling fins of old 500 KVA Transformer in Water Treatment Plant. | One Time | 220000 |  | NA
9 | Consumption of Spares | Every year | 80000
| FY 2026 -27 Total |  | 1787101.04