Annexure –D to ARR & ERC MYT petition for 2022-23to 2026-27

Capital Expenditure Plan for MYT Control Period 2022-23 to 2026-27

CSEZA Intends to undertake the capital works detailed below during the MYT control period 2022-23 to 2026-27.

| S.No | Year | Estimated Amount-Rs lakh | Financing Plan |
| --- | --- | --- | --- |
| 1 | 2022-23 | 154.55 | It is proposed to meet the expenditure from the Surplus available in CSEZA’s Power Distribution System Account |
| 2 | 2023-24 | 73 |  |
| 3 | 2024-25 | 95.9 |  |
| 4 | 2025-26 | 52.5 |  |
| 5 | 2026-27 | 38.73 |  |
| 6 | Total For MYT period | 414.68 |  |

Summary is given below;

| S.No | Description of works | Estimated amount in Rs | 22-2023 | 23-2024 | 24-2025 | 25-2026 | 26-2027 | Completion Date |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Supply, Installation, Testing and Commissioning of Smart Energy meters and prepaid energy management system. Which includes replacement of existing Energy meters with new and establishing communication facility with BEE portal as per the latest BEE regulation. -Smart meter -Software Total | 14589640 490000 15079640 | 14589640 490000 |  |  |  |  | 30-09-2023 30-09-2023 |
| 2 | Supply , Installation , testing and commissioning of New ACB Buscoupler for the Distribution Transformers 1 & 2 at SDF 17 | 21,50,000 |  |  |  | 21,50,000 |  | 30-09-2025 |
| 3 | Procurement of 1 No. 11/ 0.433KV 500 KVA USS Transformer as spare in Power distribution system. | 12,00,000 |  |  |  | 12,00,000 |  | 31-08-2025 |
| 4 | Replacement of section A side of 11 KV VCB Panel including Section A Incomer & Aux Transformer | 93,00,000 |  |  | 93,00,000 |  |  | 31-12-2024 |
| 5 | Replacement of section - B, 11 KV panel at 110 KV substation Including Section B Incomer and Bus coupler | 73,00,000 |  | 73,00,000 |  |  |  | 31-12-2023 |
| 6 | Replacement of distribution UG cable (11KV 3Cx 240 Sq.mm unearthed XLPE Aluminium cable) | 19,00,000 |  |  |  | 19,00,000 |  | 30-09-2025 |
| 7 | Procurement of thermal imaging camera | 1,50,000 | 1,50,000.00 |  |  |  |  | 31-01-2023 |
| 8 | Replacing of 30V,100Ah battery bank for control system of 1250KVA Transformer at SDF 17-Tr1 | 75,000 |  |  |  |  | 75,000 | 31-10-2026 |
| 9 | Replacing of 30V,100Ah battery bank for control system of 1250KVA Transformer at SDF 17 -Tr2 | 75,000 | 75,000 |  |  |  |  | 31-01-2023 |
| 10 | Replacing of 30V,100Ah battery bank for control system of 1250KVA distribution transformer at SD 43 | 75,000 |  |  |  |  | 75,000 | 31-10-2026 |
| 11 | Replacing of 110V,120Ah battery bank for control system of 110KV substation | 2,15,000. |  |  | 2,15,000 |  |  | 31-10-2024 |
| 12 | Replacing of 12V SMPH battery bank for5KVA UPS | 75,000 |  |  | 75,000. |  |  | 31-10-2024 |
| 13 | Purchase of two computers | 150000 | 150000 |  |  |  |  | 31.12.2022 |
| 14 | Supply Installation and Commissioning of HT cable for new Ring in 110 KV Substation | 37,22,990. |  |  |  |  | 37,22,990. | 31-12-2026 |
| Total |  |  | 15454640 | 73,00,000 | 95,90,000 | 52,50,000 | 38,72,990 |  |
| Total for MYT period from 2022-23 to 2026-27 |  |  | 41467630 |  |  |  |  |  |

Details of Capital Works planned for 2022-23

1. Supply, Installation, Testing and Commissioning of Smart Energy meters and prepaid energy management system.

Need and necessity

Bureau of Energy Efficiency Gazette notification dated 6th October, 2021 has published regulations covering mandatory annual energy auditing and also stipulating special requirements of metering and times lines to be complied by all DISCOMs. As per the above regulations DISCOMS shall meet following time lines

- Communicable Feeder metering integrated with AMI, by 31st December 2022

- All Distribution Transformers shall be metered with communicable meters. Communicable DT Metering for the following areas /consumers to be completed by December 2023

- All Industrial and commercial consumers prepaid smart consumer metering to be completed for all directly connected meters and AMR in case of other meters, by December 2023.

- BEE regulations also stipulate the electricity distribution company shall establish an information technology enabled system to create energy accounting reports without any manual interference.

Presently available energy meters are 0.5 class energy meters are being for recording the energy consumption at both HT & LT consumer points and since manufacturer has stopped production  spare meters are not available in the market for any replacement/or addition of consumers . Also the existing energy meters are not suitable for directly communicating to energy audit portal of Bureau of Energy Efficiency (BEE). Further feeder metering & Distribution transformer metering systems are not available in the existing distribution network.    In view of the above CSEZA intends to replace existing energy meters with smart meters and also provide feeder metering and DT metering to comply with the BEE regulations.

Proposed system :

All HT meters at consumer points to be replaced with 3 phase 4 wire class 0.2s Class smart meters complying to latest standards. The CT & PT at consumer points and DTs has to be replaced along with the meter with following classes, CT- 0.2s and PT- 0.2

All LT meters at consumer points to be replaced with 3 phase 4 wire class 0.5s meter complying to IS 14697 & IS 15959. The CT at consumer points has to be replaced along with the meter with class 0.5s.

GPRS / GSM modem is required establish the communication between the meter and the Meter data acquisition system.  GPRS / GSM Modems play a vital role in Automated Meter Reading (AMR) System, which shall communicate with each meter, collect data and transmit to server securely for further processing. GPRS Modem should have capability to read all makes and variants of Energy Meters which have communication capability.

Meter data acquisition system software is required to capture and maintain the electrical network topology i.e. substations, feeders (HT / LT Feeders and HT / LT Users). The software will enable capture and display of data from multi-parameter load survey analysis. Monitoring of usage/demand patterns would thus be enabled. Monitoring of peak load at different network levels could be monitored. Monitoring of performance factors like load factor, power factor, utilization factor, load duration curves would be monitored. Energy billing software will generate the monthly bill based on the data fetched from the Meter data acquisition system. Data from smart meters/system will be connected BEE Energy Audit portal so as to report Energy Accounting Report to BEE.

HT Metering cubicle with communication facility to be installed at feeder points and transformers in the distribution network to comply the BEE regulations, this will precisely quantify the distribution loss in each feeder and transformer.

Project Cost

The estimated project cost is Rs.1,50,79,640.

Benefits

- Improvement in billing accuracy

- Reduction in distribution loss

- Customized reports can be generated at any time; following are some of the standard reports.

- Instantaneous Parameters

- Load Survey Data

- Tampers / Power fail events

- Midnight Energy Data

- Billing Parameters

- Distribution loss at different voltage levels / feeders.

Project Execution Plan

Phase -1: Installation of HT Metering cubicle at Feeder’s & Distribution transformer side and establishing communication between meter and MDAS software.

Phase –2: Replacement of existing energy meters at HT consumer points and establishing communication between meter and MDAS / Billing software.

Phase –3: Replacement of existing energy meters at LT consumer points and establishing communication between meter and MDAS / Billing software.

2.	Procurement of thermal imaging camera

Objective

To procure a Thermal imaging camera for for strengthening the preventive maintenance activities

Present status

Panels/ Equipment’s Heat Build-up check-ups are not performing as a part of preventive maintenance activities.

Proposed system :

The proposal is to procure a Thermal imaging camera for strengthening the preventive maintenance activities. Thermal is a method often used to view a range of the electromagnetic spectrum that is not visible to the human eye. Thermal imaging makes use of infrared radiation that is emitted by objects. Since infrared radiation varies with temperature, thermal imaging is a useful imaging technique to pick-out objects with variable temperatures.

Components in electrical systems almost always overheat before they fail, problem areas are more easily and safely found when viewed through an IR camera.  Infrared imaging allows apparent temperatures to be seen as gradient colors, with hotter spots displayed as brighter colors, and cooler (and wetter) spots displayed as darker colors.  When a malfunctioning electrical component or connection is generating more heat than it should be, its apparent temperature will make it stand out right away when viewed through thermal imaging.

Project Cost

The approximate cost for the procurement of a Thermal Imaging Camera is approximately Rs 1.5 lakh.

Benefits

- Helps to identify problems before they cause serious failure or an electrical fire.

- Non-contact feature of Thermal imaging camera helps ensure a safe inspection.

- Thermal Imaging Camera is non-intrusive, so there is no interruption of power during the inspection.

4.	Replacing of 30V,100Ah battery bank for control system of 1250KVA Transformer at SDF 17 -Tr2

Need & Necessity

The existing battery bank for control supply to No.2 transformer 1250 KVA at SDF-17 is old and its guaranty period is expired and hence required to replace the same. The estimate cost of 30 V, 40 Ah battery bank for control system of 1250 KVA No.2Transformer at SDF-17 is Rs: 75,000/-

5   Purchase of Computers

CSEZA proposes to purchase Two Nos Computers of latest configuration and specs to be used for Power distribution System. Estimated Cost of the same is Rs 150000/-. It is requested that the same may be approved.

Details of Capital Works planned for 2023-24

1. Replacement of section - B, 11 KV panel at 110 KV substation Including Section B Incomer and Bus coupler.

Objective:

17 years Old 11KV VCB panels at 110 KV Substation has to be replaced with new VCB panels.

Present status:

Existing ABB make 11 KV VCB panels at 110 KV Substation are 17 years old and it is very difficult to get the proper spares for this out-dated model VCB. Of late frequent failures in the VCB mechanism are affecting the power system reliability in the 11 KV distribution network. There is no spare VCB available at 110KV Substation and the existing spare VCB is in beyond repair condition.

Proposed system :

The proposal is to replace the existing ABB make 11 KV feeder VCB panels of section A & section B in a phase by phase manner. As per the plan, section B VCB panel’s replacement is planned in the FY 2023-24. The removed VCB’s from section B will be utilized as spares in the section A VCB panels.

Project Cost:

The estimated project cost for section B VCB panels replacement is Rs 73 Lakh.

Details of Capital Works planned for 2024-25

1. Replacement of section A side of 11 KV VCB Panel including Section A Incomer & Aux Transformer

Objective:

17 years Old 11KV VCB panels at 110 KV Substation has to be replaced with new VCB panels.

Present status:

Existing ABB make 11 KV VCB panels at 110 KV Substation are 17 years old and it is very difficult to get the proper spares for this out-dated model VCB. Of late frequent failures in the VCB mechanism are affecting the power system reliability in the 11 KV distribution network. There is no spare VCB available at 110KV Substation and the existing spare VCB is in beyond repair condition.

Proposed system :

The proposal is to replace the existing ABB make 11 KV feeder VCB panels of section A & section B in a phase by phase manner. As per the plan, section BAVCB panel’s replacement is planned in the FY 2024-25. The removed VCB’s from section B will be utilized as spares in the section A VCB panels.

Project Cost:

The estimated project cost for section B VCB panels replacement is Rs. 93 lakh.

2. Replacing of 110V,120Ah battery bank for control system of 110KV substation

Need & Necessity

The existing 110 V, 120AH battery bank for control system of 110 KV is old and its guaranty period is expired and hence required to replace the same. The estimate cost of 110, 120 Ah battery bank for control system of 110KV substation is Rs. 2.15 lakh/-

3. Replacing of 12V SMPH battery bank for 5KVA UPS in 110kV  Substation

Need & Necessity

The existing 12V, SMPH battery bank for 5kVA UPS in 110kV Substation its guaranty period is expired and hence required to replace the same. The estimate cost for the same is Rs. 75000/-

Details of Capital Works planned for 2025-26

1.Supply , Installation , testing and commissioning of  New ACB Buscoupler for  the Distribution Transformers 1 & 2 at SDF 17

Objective

Bus coupling provision to be enabled in between Transformer 1 & 2 at SDF # 17 for increasing the reliability of power distribution at SDF - 17

Present status

Bus coupler was not considered in the initial design of SDF – 17 LT Switchboard, as a result of this if there is any maintenance or fault occurred in any of the transformers that section is in an isolated condition.  Transformer preventive maintenance works are always scheduled on Sundays only because of the mentioned reason. But few companies are working in 24x7 manner, these power shutdowns are adversely affecting the productivity of that companies and our Annual preventive maintenance plan.

Proposed system :

The proposal is to install a bus coupler panel in between the Transformer 1 & 2 at SDF 17. Bus coupler is a breaker used to couple two Bus bars for transferring the load from one bus to another. When transformer is to be taken for maintenance or if there is any fault in any of the transformer the corresponding circuit breaker should be switched off but there is a requirement for constant power delivery, so the bus coupler has to be closed to route the power from one bus to other and thereby we can increase the system reliability.

We can utilize the bus coupler panel as an energy saving option during light load periods like weekends & public holidays. One transformer can withstand the entire load during the mentioned period, the bus coupler will couple the two buses and we can switch off any one of the transformers, thereby we can save the energy consumption occurring due to loss in the Transformer.

Project Cost

The estimated project cost is 21, 50,000/-

Benefits

- Power supply reliability will be improved.

- Energy Savings

- Transformer maintenance can be scheduled as desired.

2. Procurement of 1 No. 11/ 0.433KV 500 KVA USS Transformer as spare in Power distribution system

Objective

To procure a 500 KVA Unitised Sub-Station (USS) as a common spare for the power distribution system in the entire zone area.

Present status

There is no spare transformer available for the entire distribution system comprising with following transformers

Proposed system :

The proposal is to procure a 500 KVA Unitised Sub-Station (USS) as a common spare for the power distribution system in the entire zone area. A USS comprises of various sub-station equipments housed inside a metal enclosure. The equipments include a step down transformer, a Vacuum Circuit Breaker (VCB) or a Ring Main Unit (RMU) on High Voltage (HV) side and Low Voltage (LV) distribution panel in LV side compartment. It is a pre-fabricated sub-station engineered to reduce size, increase safety.

The proposed USS can be used as a common spare in the distribution system except SDF 17 & 43. In SDF 17 if we are providing bus coupling system there is no need of any spare.

Project Cost

The project cost for the procurement of a 500 KVA Unitised Sub-Station (USS) is approximately Rs 12 Lakhs.

Benefits

- Installation & Charging will be very simple

- Space constrains in the existing location will not affect the installation of USS

- USS with a trolley arrangement will overcome the transportation difficulties during shifting.

3 .Replacement of distribution UG cable (11KV 3Cx 240 Sq.mm unearthed XLPE Aluminium cable

Objective

To replace the existing deteriorated 11 KV Distribution earthed UG cable with unearthed UG cable.

Present status

Feeder cable insulation resistance values of the following feeders  are found to be low low during our annual preventive maintenance check-up, which may lead to cable failure in near future.

| Sl No | Feeder | Insulation resistance value in M Ohms |  |  |
| --- | --- | --- | --- | --- |
| 1 | Substation 1(B) to RMU 1 B4 | 100 | 50 | 150 |
| 2 | RMU 3D1 to RMU 3B3 | 150 | 50 | 150 |

Proposed system :

The proposal is to replace the existing deteriorated XLPE earthed UG HT cable with XLPE unearthed UG HT cable. Unearthed cable has more insulation strength as compared to earthed cable,in earthed  cable the insulation level between conductor to armour is 0.57 times of the insulation level between the conductor to conductor but in unearthed cable the insulation level of conductor to armour is equal to the insulation level of conductor to conductor , which will enable increased level of insulation.

Project Cost

The estimated project cost for the same is 19 lakh.

Benefits

- Sudden breakdowns can be avoided, down time of such breakdowns may extend up to few weeks

- Feeder insulation level will be improved

Details of Capital Works planned for 2026-27

1. Replacing of 30V,100Ah battery bank for control system of 1250KVA  Transformer  at SDF 17-Tr1

Need & Necessity

The existing battery bank for control supply to No.1 transformer 1250 KVA at SDF-17 is old and its guaranty period is expired and hence required to replace the same. The estimate cost of 30 V, 100 Ah battery bank for control system of 1250 KVA No.1Transformer at SDF-17 is Rs: 75,000/-

2. Replacing of 30V,100Ah battery bank for control system of 1250KVA distribution transformer at SD 43

Need & Necessity

The existing battery bank for control supply to No.1 transformer 1250 KVA at SDF-43is old and its guaranty period is expired and hence required to replace the same. The estimate cost of 30 V, 100 Ah battery bank for control system of 1250 KVA No.1Transformer at SDF-43 is Rs: 75,000/-.

3. Supply Installation and Commissioning of HT cable for new Ring  in 110 KV Substation

Objective:

To avoid over loading on ring # 3, split the existing ring and add a new ring.

Present status:

Existing ring 3 getting over loaded at times and most of the times the ring is in full load condition which will lead to ring failure.

Proposed system :

The proposal is to lay a new cable from substation and split the existing ring 3 by removing two RMU’s from the ring 3 and connect them with new cable, thereby we can add a new ring (Ring 4) in the system, which will avoid the overloading on the existing ring 3.

Project Cost:

Estimated Cost of the Project is Rs 37.23.Lakh

Benefits

- Overloading on the existing ring # 3 can be avoided.

- It is possible to add more RMU’s in the system if there is any further power demand.